INVITATION TO TENDER

Ukraine

Construction works on project «Capital repairs of individual heating substations and heating systems in public buildings of Kyiv»

INVITATION TO TENDER

This invitation to tender follows General announcement of procurement for this Project which was published on 28 April 2020 on NEFCO`s website in Procurement section subsection Procurement notices (https://www.nefco.org/procurements/ )

UKRAINE EXECUTIVE BODY OF KYIV CITY COUNCIL KYIV CITY STATE ADMINISTRATION MUNICIPAL ENTERPRISE “PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT” (ME “PIU”) – hereinafter referred to as “Employer”, intends to use part of the proceeds of a loan from the Nordic Environment Finance Corporation (NEFCO) towards Contract payment «Construction works on Project «capital repairs of individual heating substations and heating systems in public buildings of Kyiv», Lot 8.1 (11 sites)».

The Employer now invites sealed tenders from Contractors for the following contract to be funded from NEFCO loan for purchasing, shipment of materials for construction works on capital repairs of individual heating substations and heating systems in 11 public buildings of Kyiv (the list and building addresses, as well as the types of works for each buildings, are provided in Section ІV. Employer’s requirements).

Tendering for contracts that are to be financed with the proceeds of NEFCO financing is open to firms from any country

To be qualified for the award of a contract, tenderers must satisfy the following minimum criteria:

- Tenderers must meet eligibility requirements stated in Instructions to Tenderers (ITT) , article 4 (as stated in tender proposal letter):

  - not to have conflict of interest, as stated in  ITT, 4.3;

  - not to be defined as ineligible as a consequence of non-compliance with the requirements stated in ITT 4.4;

- The Tenderer, has the financial, technical and production capability and capacity necessary to perform the Contract  and Tenderer’s average annual revenue in the previous 3 (three) full years (2019, 2020, 2021) was at least 29,4  mil UAH. In case of tender submitted by JVCA, the leading partner should demonstrate at least 60% compliance with the requirement.

- The Tenderer has satisfactorily executed similar works to customers and successfully completed at least three (3) similar contracts during any of 2019, 2020, 2021, 2022, 2023 years for the total amount of minimum 14,6 mil UAH.

- The Tenderer or its agent will be able to carry out warranty obligations;

- The Tenderer is not bankrupt or under insolvency or bankruptcy procedures according to the national legislation or regulations;

While preparing offers, the Tenderers should take into account that the works in this contract will tentatively last for 120 days from the date contract signing.

Tender documents can be acquired free of charge from Employer at address provided below after receiving written request from prospective Tenderer.

Tender Documents, upon request from prospective Tenderer will be sent by email in electronic format (PDF file) immediately (during 2 days), however the sender is not responsible for loss or late delivery.

Pre-tender meeting of Tenderers with the Employer for discussion of technical and procedural issues will be held on 12:00, «15» February 2024 address: 3A, B. Khmelnitskogo Street, Kyiv 01001, ME «PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT», office №307. Meeting will be organized remotely with web-based tools – the Employer will notify all interested participants additionally about this.

Tender documents are published on ME “PIU” website http://kyivesko.com.ua for general availability and can be acquired free of charge by any physical or legal person.

All tenders must be accompanied by a tender security in the form of declaration guarantee, the form of which is contained in the tender documents. The purpose of tender security is to ensure the tenderers are serious about their participation.

Successful Tenderer must provide Contract performance guarantee from a reputable bank acceptable to NEFCO in form provided by Section VII «Contract forms» of Tender document.

Tender proposals must be delivered to the office at the address listed below and before 9:30 06 March 2024, further they will be opened in the presence of those tenderers’ representatives who choose to attend tender opening.

Prospective tenderers may obtain further information from, and also inspect and acquire the tender documents at, the following office:

Sklyarenko Valentyna Vadymivna – head of public procurement sector

Customer:   UKRAINE EXECUTIVE BODY OF KYIV CITY COUNCIL KYIV CITY STATE ADMINISTRATION MUNICIPAL ENTERPRISE “PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT”

Address: office № 305, 3A, B. Khmelnitskogo Street, Kyiv 01001

Phone: (044) 234-54-10 (27)

Email: v.sklyarenko@kyivesko.com.ua.

Orlenko Serhii Volodymyrovych, customer`s representative (on technical matters)

Customer:   UKRAINE EXECUTIVE BODY OF KYIV CITY COUNCIL KYIV CITY STATE ADMINISTRATION MUNICIPAL ENTERPRISE “PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT”

Address: office № 305, 3A, B. Khmelnitskogo Street, Kyiv 01001

Phone: (044) 234-54-10 (27)

Email: adc@kyivesko.com.ua

Date 05 February 2024

Tender Document for

Procurement of

Works

Procurement of:

Construction works on project «Capital repairs of individual heating substations and heating systems in public buildings of Kyiv»

Issued on: 05 February 2024

Tender No: Lot 8.1

Employer: UKRAINE EXECUTIVE BODY OF KYIV CITY COUNCIL KYIV CITY STATE ADMINISTRATION MUNICIPAL ENTERPRISE “PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT”

Country: Ukraine

Tender document

List of contents

Section I.  Instructions to Tenderers	5

Section II. Evaluation and Qualification Criteria	15

Section IІІ. Tender Forms	18

Section ІV. Employer`s requirements	37

Section V. General Conditions of Contract	75

Section VI. Particular Conditions of Contract	91

Section VIІ. CONTRACT FORMS	95

Section I. Instructions to Tenderers

|  | General provisions |  |  |  |
| --- | --- | --- | --- | --- |
| - Scope of Tender | 1.1 The Employer, UKRAINE EXECUTIVE BODY OF KYIV CITY COUNCIL KYIV CITY STATE ADMINISTRATION MUNICIPAL ENTERPRISE “PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT” issues this Tender document for procurement of: Construction works on project «Capital repairs of individual heating substations and heating systems in public buildings of Kyiv», Lot 8.1 (11 sites), as stated in Section IV Employer`s requirements. |  |
|  | - Unless otherwise stated, throughout this Tender Document definitions and interpretations shall be as prescribed in Section V, General Conditions of Contract |  |
| - Source of Funds | - The Borrower (hereinafter called «the Borrower») of the Norfic Environment Finance Corporations’ s (hereinafter “ the NEFCO”) financing, UKRAINE EXECUTIVE BODY OF KYIV CITY COUNCIL KYIV CITY STATE ADMINISTRATION MUNICIPAL ENTERPRISE “PROJECT IMPLEMENTATION UNIT FOR THE KYIV PUBLIC BUILDING ENERGY EFFICIENCY PROJECT”, requested funding toward the cost of the project «Capital repairs of individual heating substations and heating systems in public buildings of Kyiv». The Borrower intends to utilize a portion of the funds to eligible payments under the stated contract for which this Tender Document is issued. |  |
|  | - Payments by NEFCO will be made only at the request of the Borrower and upon approval by NEFCO in accordance with the terms and conditions of the financing agreement between the Borrower and NEFCO (hereinafter called the “Loan Agreement”), and will be subject in all respects to the terms and conditions of that agreement |  |
| - Prohibited Practices | 3.1 NEFCO requires that Grant Beneficiaries/Recipients (including beneficiaries of NEFCO financing), as well as tenderers, suppliers, subsuppliers, contractors, subcontractors, concessionaires, consultants and subconsultants under NEFCO financed contracts, observe the highest standard of ethics during the procurement and fulfilment of their contract obligations. In pursuance of NEFCO's Anti-Corruption Policy (as defined in Clause 2 of Section V of the General Conditions of Contract), NEFCO: - (a) defines, for the purposes of this provision, Prohibited Practices as one or more of the following: - (a) defines, for the purposes of this provision, the terms set forth below as follows: #### (i) “Abuse” means theft, misappropriation, waste or improper use of property or assets related to the Contract, either committed intentionally or through reckless disregard; #### (ii) “Coercion” means impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party for the purpose of improperly influencing the actions of a party; #### (iii) “Collusion” means an arrangement between two or more parties designed to achieve an improper purpose, including for the purpose of improperly influencing the actions of another party; #### (iv) “Corruption” means meaning the promise, offering, giving, receiving, or soliciting, directly or indirectly, anything of value or any undue advantage, or any act or omission that involves the abuse of authority or functions, for the purpose of influencing or causing to influence improperly the actions of another party, or for the purpose of obtaining an undue advantage for oneself or for another party; - “Fraud” means meaning any act or omission, including misrepresentation or concealing a material fact, that knowingly or recklessly misleads, or attempts to mislead, a party for the purpose of obtaining a financial or other benefit or undue advantage for oneself or for a third party, or to avoid an obligation; - “Obstruction” means #### (a) deliberately destroying, falsifying, altering or concealing evidence material to an investigation; #### (b) making false statements to investigators in order to materially impede an investigation; #### (c) failing to comply with requests to provide information, documents or records in connection with an investigation; #### (d) threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to a NEFCO investigation or from pursuing an investigation; or #### (e) materially impeding NEFCO’s contractual rights of audit or access to information; and - “Money Laundering” means #### (a) the conversion or transfer of property, knowing that such property is derived from criminal activity, to conceal and disguise the illicit origin of the property, or assisting any person who is involved in the commission of such activity to evade the legal consequences of this action; #### (b) the concealment or disguise of the true nature, source, location, disposition, movement, rights with respect to, or ownership of property, knowing such property is derived from criminal activity; #### (c) the acquisition, possession or use of property knowing, at the time of receipt, that such property was derived from criminal activity; or #### (d) participation or assistance in any of the activities above; and - (viii) “Financing of terrorism” means the provision or collection of funds, by any means, directly or indirectly, with the intention that they should be used or in the knowledge that they are to be used, in full or in part, in order to carry out terrorist activities (the "terrorist activities" shall have the same meaning as set out in Article 2 of the International Convention for the Suppression of the Financing of Terrorism). (b) will reject a proposal for award if it determines that the tenderer, supplier, subsupplier, contractor, subcontractor, concessionaire, consultant or subconsultant recommended for award has engaged in Prohibited Practices in competing for the contract in question; (c) will cancel the portion of NEFCO financing allocated to a contract for Works if it at any time determines that Prohibited Practices were engaged in by representatives of the Borrower/Grant Beneficiary or of other beneficiary of NEFCO financing during the procurement or the execution of that contract, without the Borrower/Grant Beneficiary having taken timely and appropriate action satisfactory to NEFCO to remedy the situation; (d) may declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a NEFCO-financed contract if it at any time determines that the firm has engaged in Prohibited Practices in competing for, or in executing, a NEFCO -financed contract; and (e) reserves the right, where a Borrower/Grant Beneficiary or a firm has been found by a judicial process in any country or a finding by the enforcement (or similar) mechanism of another international organisation, including Mutual Enforcement Institutions, to have engaged in Prohibited Practices (i) to cancel all or part of NEFCO financing for such Borrower/Grant Beneficiary; and (ii) to declare that such a firm is ineligible, either indefinitely or for a stated period of time, to be awarded a NEFCO-financed contract; and - f) will have the right to require that, in contracts financed by NEFCO, a provision be included requiring suppliers, subsuppliers, contractors, subcontractors, concessionaires, consultants and sub-consultants to permit NEFCO to inspect their accounts and records relating to the performance of the contract and to have them audited by auditors appointed by NEFCO. |  |
|  | 3.2 Furthermore, tenderers shall be aware of the provisions stated in Section V, General Conditions of Contract and Section VI, Particular Conditions of Contract. |  |
| - Eligible Tenderers | - A Tenderer may be a natural person, private entity, government-owned entity—subject to Instructions to Tenderers (hereinafter referred to as “ITT”) 4.3—or any combination of such entities in the form of a joint venture, consortium, or association (JVCA). In the case of JVCA: - all partners shall be jointly and severally liable when participating in the tender process and implementing the Contract; - the JVCA shall nominate from the partners/members of JVCA a single Representative (Lead Partner) who shall have the authority to conduct all businesses for and on behalf of any and all the partners/members of the JVCA during the Tender process and, in the event the JVCA is awarded the Contract, during contract execution. |  |
|  | - NEFCO permits firms and individuals from all countries to offer Works for NEFCO-financed contracts. - Consistent with international law, the proceeds of the NEFCO’s loans, equity investment or guarantees shall not be used for payment to persons or entities or for any import of Hardware, if such payment or import is prohibited by EU sanctions and a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations. Persons or entities, or Contractors offering Plants and Works, covered by such prohibition should therefore not be eligible for the award of NEFCO-financed contracts. 4.3 A Tenderer shall not have a conflict of interest, as defined in sub-causes 3.27, 3.28 and 3.29 of the NEFCO’s Procurement Policy and Procedures. All Tenderers found to have a conflict of interest shall be disqualified. - 4.4. Firms shall be excluded if: - as a matter of law or official regulation, the Recipient’s country prohibits commercial relations with that country or imposes sanctions on such firms, provided that NEFCO is satisfied that such exclusion does not preclude effective competition; - a firm or individuals representing the firm are subject to EU economic sanctions, as published in the Official Journal of European Union. - by an act of compliance with a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations, the Borrower’s/Grant Beneficiary’s country prohibits any import from that country or any payments to persons or entities in that country. |  |
| - Eligible Plant and Related Works | 5.1 All Works and materials to be supplied under the Contract and financed by NEFCO, shall have as their country of origin an eligible country in accordance with ITT 4.2. 5.2 For purposes of this paragraph, the term Materials includes commodities and raw materials; and Works includes works such as transportation, construction, installation, commissioning and training. |  |
|  | Preparation of Tenders |  |
| - Cost of Tendering | - The Tenderer shall bear all costs associated with the preparation and submission of its Tender, and the Employer shall not be responsible or liable for those costs, regardless of the conduct or outcome of the tendering process. - A prospective Tenderer requiring any clarification of the Tender Document shall contact the Employer in writing by sending his written request to the address: 3-A B. Khmelnitskogo Street, Kyiv 01001, contact person: Sklyarenko Valentyna Vadymivna, e-mail: v.sklyarenko@kyivesko.com.ua; Orlenko Serhii Volodymyrovych, customer representative (on technical matters), e-mail: adc@kyivesko.com.ua . The Employer responds to any request for clarification tender document during one workweek, provided that such request is received prior to 20 February 2024. Response shall be in writing with copies to all Tenderers who have received the Tender Document, including a description of the inquiry but without identifying its source. Should the Employer deems it necessary to amend the Tender Document as a result of a request for clarification, it shall do so. - Tenderer can visit and inspect sites and view Tender document and receive all necessary information for themselves which is needed for Tender proposal and Contract conclusion. Site visiting shall be carried out at the expense of the Tenderer. Site visiting should be agreed with Employer beforehand for each Tenderer. - The Tenderer’s designated representative is invited to attend a pre-tender meeting (online meeing) to be held on 12:00 15 February 2024 [The online meeting will be organised remotely via web tools - the Employer will additionally inform all Tenderers who express interest in participating in the tender]. The purpose of the meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage. - The Tenderer is requested, as far as possible, to submit any questions in writing, to reach the Employer not later than one week before the meeting. - Minutes of the pre-tender meeting, including the text of the questions raised, and the responses given, together with any responses prepared after the meeting, will be transmitted promptly to all Tenderers who have obtained the Tender Document. Any changes to the Tender Document that may become necessary as a result of the pre-tender meeting shall be made by the Employer exclusively through the issue of an Addendum and not through the minutes of the pre-tender meeting. - Nonattendance at the pre-tender meeting will not be a cause for disqualification of a Tenderer. |  |
| - Language of Tender | - Tenders from foreign companies should be prepared in English language with translation in Ukrainian. Tenders from Ukrainian companies should be prepared in Ukrainian with translation in English. The supporting documents do not need to be translated. |  |
| - Documents Comprising the Tender | 8.1 The Tender shall comprise the following: - letter of Tender and Covenant of Integrity in a form provided in Section III Tender Forms; - completed Price Schedules as provided in Section III, Tender Forms; - tender-security , in accordance with ITT 15; |  |
|  | - written confirmation authorising the signatory of the Tenderer to commit the Tender; - documentary evidence establishing the eligibility of the Materials and Works offered by the tenderer in accordance with clause 13 of ITT; - documentary evidence establishing the Tenderer’s qualifications in accordance with the requirements of Section II, Evaluation and Qualification Criteria, using the relevant forms provided in Section III, Tender proposal forms; - documentary evidence, establishing the conformity of the Materials and Works offered by the Tenderer with the Tender Document, using the relevant forms provided in Section III, Tender proposal forms and Section IV; - in the case of a Tender proposal submitted by a Joint Venture, Consortium or Association (JVCA), the JVCA agreement, complying with the requirements of Clause 4 of ITT and indicating at least the parts of the Employer’s Requirements to be executed by the respective partners. |  |
| - Alternative Tenders - Tender Prices and Discounts | - Alternative technical proposals shall not be considered - 10.1 The prices quoted by the Tenderer in the Letter of Tender and in the Price Schedules should be fixed. - 10.2 Notwithstanding with any other provision in this tender document the Materials to be supplied from outside Ukraine shall be delivered DDP at Site, Incoterms 2020 and the Materials to be supplied from Ukraine shall be delivered at Site. The tenderer shall quote the price of the goods the following way: - For hardware delivered from outside of Ukraine tender price shall be DDP with delivery to Site; - For Hardware delivered from inside Ukraine, tender price should be – with delivery to Site. - The Works can include the preparation of drawings, construction, installation, commissioning of the Works to the Employer, and other works required by the Employer requirements and Price-lists. - 10.3 Prices provided by Tenderer must be fixed on the moment of Contract execution are not subject to changes under any circumstances. Tender submitted with revised price which doesn’t match this clause shall be rejected by Employer as inconsistent. |  |
| - Currencies of Tender proposals | - Tenderers should put all prices in Hryvnya. |  |
| - Documents Establishing the Qualifications of the Tenderer | - To establish its qualifications to perform the Contract, the Tenderer shall provide the information requested in Section III, Tender proposal forms. - 12.4 Tenderers are responsible for the contend of Tender proposals and are obliged to provide guarantee letter on abiding the current Ukrainian legislation in force in their work, including: - - Law of Ukraine "About sanctions" from 14.08.2014р. № 1644-VII (with changes); - - Decree of the president of Ukraine from 19.03.2019р. №82/2019 «About decision of National security and defense council of Ukraine from 19 march 2019 «About implementation, abolition and making changes into personal special economic and other restrictive (sanctions)»; - - Decree of the president of Ukraine from 15 may 2017р. №133/2017; - - Resolution of Cabinet of Ministers of Ukraine from 07.11.2014р. №595 «Some matters of funding budgetary institutions, providing social benefits and providing financial assistance to some enterprises and organizations of Donetsk and Lugansk regions» (with changes); - - Resolution of Cabinet of Ministers of Ukraine from 16.12.2015р. №1035 «About restrictions in shipment of separate goods (works, services) from temporary occupied territories on other part of Ukraine and/or from other territory of Ukraine on temporary occupied territory» (taking into account Kyiv appeal administrative Court order № 826/9502/16 from 14.06.2017); - - Resolution of Cabinet of Ministers of Ukraine from 30.12.2015р. № 1147 «About prohibition of importing on Ukrainian customs territory goods of Russian Federation origin» (with changes). - In case of changes in documents mentioned above tenderers should be guided by, their actual versions/editions on date of tender proposal. - Tenderers to which have been applied sanctions according to above mentioned legislation act shall be rejected. |  |
| - Documents Establishing the Eligibility of Works | - To establish the eligibility of the Works and Materials, Tenderers shall complete the forms, included in Section IІІ, Tender Forms. - 13.2 The Tenderer must provide the following documentary evidence to establish the conformity of the Works and Materials: - The Materials and Works documentary evidence of conformity to the tender documents may be in the form of literature, drawings and data, and shall consist of: - (a) a detailed description of the essential technical and performance characteristics of the Plant; - (b) a paragraph-by-paragraph commentary on the Employer’s Requirements demonstrating substantial responsiveness of the Plant and Works to those specifications or a statement of deviations and exceptions to the provisions of the Employer’s Requirements. |  |
| - Validity of Tenders | - Tender proposals shall remain valid 120 days after the tender submission deadline date. A tender valid for a shorter period shall be rejected as nonresponsive. - In exceptional circumstances, prior to the expiration of the Tender validity period, the Employer may request Tenderers to extend the period of validity of their tenders. The request and the responses shall be made in writing |  |
| - Tender Security | 15.1. The Tenderer shall provide as part of its tender, the original of a tender security using the form included in Section ІІІ Tender Forms. 15.2 Any Tender not accompanied by a substantially responsive tender security shall be rejected by the Customer as nonresponsive. |  |
| - Finalization and signing of Tender | - The Tenderer shall prepare one original of the documents comprising the tender and clearly mark it “ORIGINAL.”. - In addition, the Tenderer shall include into its Tender an electronic copy of its complete Tender in a form of the scanned document in a PDF format and other electronic versions of the documents, which are required by the tender documentation, on flash memory stick. |  |
|  | - The original of the Tender proposal shall be typed or written in indelible ink and shall be signed by a person duly authorised to sign on behalf of the Tenderer. This authorisation shall be confirmed by the Tenderer’s statutory documents attached to the Tender proposal. |  |
|  | - A Tender proposal submitted by a JVCA shall comply with the following requirements: |  |
|  | - (a) It shall be signed so as to be legally binding on all partners; |  |
|  | - (b) Include the Representative’s authorisation, consisting of a power of attorney signed by those legally authorised to sign on behalf of the JVCA. |  |
|  | Submission and Opening of Tender proposals |  |
| - Submission and marking envelopes with tender | - Tenderers may always submit their Tender proposals by mail or by hand. Procedures for submission, sealing and marking are as follows: |  |
|  | - Customer`s address: 3-A B. Khmelnitskogo Street office 305, Kyiv 01001 |  |
|  | - The inner and outer envelopes should: - bear the name and address of the Tenderer; - be addressed to the Employer; - bear the specific identification of this Tendering process pursuant to ITT 1.1; |  |
|  | - bear a warning: “Do not open before [10:30 06 March 2024]” |  |
|  | - If envelopes and packages are not sealed and marked as required, the Employer will assume no responsibility for the misplacement or premature opening of the Tender. |  |
| - Deadline for Tender Submission | - Tenders must be received by the Employer at the specified address and no later than [9:30 06 March 2024] |  |
| - Tender Opening | - The Employer shall conduct the Tender opening in public, in the presence of Tenderers` designated representatives (as well as anyone else) that choose to attend, and at the address specified in 17.1(a) above immediately after deadline specified for submission of tenders in 18.1 above. |  |
|  | Evaluation of Tender proposals |  |
| - Confidentiality | - Information relating to the evaluation of Tenders shall not be disclosed to Tenderers or any other persons not officially concerned with such process until information on Contract award is communicated to all Tenderers. |  |
|  | - Any attempt by a Tenderer to influence improperly the Employer in the evaluation of the Tender or Contract award decisions may result in the rejection of its Tender. |  |
|  | - Notwithstanding ITT 20.1, from the time of Tender opening to the time of Contract award, if any Tenderer wishes to contact the Employer on any matter related to the Tendering process, it should do so in writing. |  |
| - Clarification of Tenders | - The Employer may, at its discretion, ask any Tenderer for a clarification of its Tender, to be provided within 5 (five) days. The Employer’s request for clarification and the response shall be in writing. No change in the prices or substance of the Tender shall be sought, offered, or permitted, except to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Tenders. |  |
|  | - If a Tenderer does not provide clarifications of its Tender by the date and time set in the Employer’s request for clarification, its Tender may be rejected. |  |
| - Determination of compliance |  | - The Employer’s determination of a Tender’s responsiveness is to be based on the contents of the Tender itself, as defined in ITT 8. |  |
|  |  | - A substantially responsive Tender is one that meets the requirements of the Tender Document without material deviation, terms, or omission. |  |
|  |  | - “Deviation” is a departure from the requirements specified in the Tender Document; |  |
|  |  | - “Terms” is the setting of limiting conditions or withholding from complete acceptance of the requirements specified in the Tender Document; |  |
|  |  | - “Omission” is the failure to submit part or all of the information or documentation required in the Tender Document. |  |
|  |  | - A material deviation, terms, or omission is one that |  |
|  |  | (a) if accepted, would: |  |
|  |  | (i) affect in any substantial way the scope, quality, or performance of the Employer’s Requirements as specified in Section IV; |  |
|  |  | (ii) limit in any substantial way, inconsistent with the Tender Document, the Employer’s rights or the Tenderer’s obligations under the proposed Contract; |  |
|  |  | (b) if rectified, would unfairly affect the competitive position of other Tenderers presenting substantially responsive Tenders. |  |
|  |  | - If a Tender is not substantially responsive to the requirements of the Tender Document, it shall be rejected by the Employer and may not subsequently be made responsive by correction of the material deviation, terms or omission. |  |
|  |  | - Provided that a Tender is substantially responsive, the Employer may waive any quantifiable nonconformity in the Tender that does not constitute a material deviation, terms or omission. The cost of all quantifiable deviations or omissions shall be added to the tender price in question. A reasonable estimate of the cost will be made by the Employer, taking into consideration the corresponding tender prices of other responsive tenderers or other appropriate market prices. Such costs will be at the Employer’s sole discretion. A Tenderer will not be requested or permitted to offer a price adjustment for rectifying such deviations or omissions. - Provided that a Tender is substantially responsive, the Employer may request the Tenderer to submit any necessary missing information or documentation, within a reasonable period of time, to rectify nonmaterial nonconformities in the Tender. Requested information or documentation on such nonconformities shall not be related to any aspect of the price of the Tender. Failure of the Tenderer to comply with the request may result in the rejection of its Tender. - 22.7 Employer has right to apply for confirmation on information provided by Tenderer to government authorities, enterprises, institutions, organizations according to their competence. In case of acquirement of reliable information about nonconformity to qualification criteria, existence of reasons or fact of any false information in Tender, which is substantial for Tender evaluation, Employer may reject Tender of such Tenderer. |  |
|  |  | - Tender Evaluation and Comparison |  |
| - Qualification of the Tenderer |  | - 23.1 The Employer shall determine whether the Tenderers meet the qualifying criteria specified in Section II, Evaluation and Qualification Criteria. Tenders not meeting the qualification criteria shall be rejected. |  |
| - Evaluation and Correction of Mathematical Errors |  | - 24.1 The Employer shall use the criteria and methodologies indicated in Section II, Evaluation and Qualification Criteria. No other evaluation criteria or methodologies shall be permitted. |  |
|  |  | - 24.2 Provided that the Tender is substantially responsive, the Employer shall correct arithmetical errors as indicated in Section II. Evaluation and Qualification Criteria.. - 24.3 If a Tenderer does not accept the correction of errors, its Tender shall be declared non-responsive. - 24.4 In the event that a tender is identified during the evaluation process as being considered as abnormally low and the tenderer is subsequently unable to demonstrate beyond reasonable doubt through a clarification process its capability to perform the contract for the offered price, the tender may be rejected subject to prior no-objection by NEFCO. - 24.5 Tender evaluation and comparison and a subsequent contract award shall be carried out in line with NEFCO’s Tender Evaluation Guide.. |
| - Tender Adjustments |  | - 25.1 For the evaluation and comparison purposes the Employers shall adjust the Tender prices using the methodology specified in Sub-clause 22.5 ITT above. |  |
| - Customer ’s right to accept or reject any or all Tenders. | - 26.1 The Employer reserves the right to accept or reject any Tender, and to annul the Tendering process and reject all Tenders at any time prior to contract award, without thereby incurring any liability to Tenderers. In case of annulment, all Tenders submitted and specifically Tender securities shall be promptly returned to the Tenderers. |  |
|  |  | - Contract award criteria |  |
| 27. Award Criteria |  | - 27.1 The Employer will award the Contract to the Tenderer whose offer has been determined to be the lowest evaluated Tender and is substantially responsive to the Tender Document, provided further that the Tenderer is determined to be qualified to perform the Contract satisfactorily. |  |
| - Variation of quantities at time of award. | - 28.1 The Employer reserves the right at the time of award of the contract to increase or decrease the scope of works specified in the Section ІV «Employer`s requirements», up to 15%, percentage, without any change in the unit rates or prices for goods or services or other Contract terms and conditions. |  |
| - Notification of Award |  | - 29.1 Prior to the expiration of the period of Tender validity, the Employer shall notify the successful Tenderer, in writing, that its Tender proposal has been accepted. |  |
|  |  | - 29.2 Until a formal Contract is prepared and executed, the notification of award shall constitute a binding Contract. |  |
|  |  | - 29.3 At the same time, the Employer shall also notify all other Tenderers of the results of the Tendering, identifying the name of the winning Tenderer and the price it offered. After receiving this notification, the unsuccessful Tenderers may request in writing to the Customer for a debriefing seeking explanations on the grounds on which their Tenders were not selected. The Employer shall promptly respond in writing (during 7 working days) to any unsuccessful Tenderer who requested a debriefing. |  |
| - Signing of Contract |  | - 30.1 Promptly upon notification, the Employer shall send the successful Tenderer the Contract for signing. |  |
|  |  | - 30.2 Within twenty-eight (28) days of receipt of the Contract Agreement, the successful Tenderer should sign, date, and return it to the Employer. |  |
| 31. Performance Security |  |  |  | - 31.1 Within twenty-eight (28) days of the receipt of notification of award from the Employer, the successful Tenderer should provide the performance security in accordance to conditions of the Contract. |  |
|  |  |  |  | - 31.2 Failure of the successful Tenderer to submit the above-mentioned Performance Security or sign the Contract shall constitute sufficient grounds for the annulment of the award. In that event the Employer may award the Contract to the next lowest evaluated Tenderer whose offer is substantially responsive and is determined by the Employer to be qualified to perform the Contract satisfactorily. |  |

| Section II. Evaluation and Qualification Criteria |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| This section includes all criteria which Employer should utilize for evaluation of Tender proposals and definitions of qualification of Tenderers. According to IIT all different factors, methods or criteria should not be utilized. Tenderer should provide all information required by forms included in Section ІІІ Tender Forms. А. Evaluation Criteria and Methodology |  |  |  |  |
|  |  | The evaluation of Tenders and the correction of arithmetical errors shall be undertaken by the Employer in accordance with the following methodology: |  |  |  |
| 1) |  | Establishing the Qualification |  |  |  |
|  |  | The Employer shall establish whether the Tenderers are qualified to perform the Contract in accordance with the provisions of paragraph B: Qualification Criteria below. If the Tenderer is determined to be qualified to perform the Contract in accordance with 23.1 ITT it shall be determined as eligible for Contract award. |  |  |  |
| 2) |  | Discounts |  |  |  |
|  |  | The Employer will adjust the Tender Price, using the methodology prescribed by the Tenderer in its Letter of Tender, to taking into account Discounts offered by the Tenderer as read out during the Tender Opening. In the event of any ambiguity in the Tenderer’s methodology, the benefit of the doubt shall be given to the Employer. If a Tenderer does not accept the Employer’s determination, its tender shall be declared non-responsive. The discount methodology prescribed by the Tenderer cannot be anyhow related or tied to tender proposals of other Tenderers. |  |  |  |
| 3) |  | Correction of Mathematical Errors |  |  |  |
|  |  | (a) Where there are errors between the total of the amounts given under the column for the price breakdown and the amount given under the Total Price, the former shall prevail and the latter will be corrected accordingly; |  |  |  |
|  |  | (b) If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price shall prevail and the total price shall be corrected, unless in the opinion of the Employer there is an obvious misplacement of the decimal point in the unit price, in which case the total price as quoted shall govern and the unit price shall be corrected; |  |  |  |
|  |  | (c) If there is an error in a total corresponding to the addition or subtraction of subtotals, the subtotals shall prevail and the total shall be corrected; |  |  |  |
|  |  | - If there is a discrepancy between words and figures, the amount in words shall prevail, unless the amount expressed in words is related to an arithmetic error, in which case the amount in figures shall prevail subject to (a) and (b) above. |  |  |  |
| 4) |  | Detailed Evaluation |  |  |  |
|  |  | Following the completion of 1) - 2) above, the Employer shall subject only the Tender proposals that were not rejected in the above-described steps 1) – 2) to a detailed evaluation to determine whether these the Tender proposals are substantially responsive to the tender documents in accordance with the provisions of Clause 22 ITT. In doing so, the Employer shall follow the procedure described in NEFCO’s Tender proposal Evaluation Guide. |  |  |  |
| 5) |  | Reassessment of Tender Ranking |  |  |  |
|  |  | In the event that the lowest priced the Tender proposals is determined to be substantially responsive in accordance with the provisions of Clause 22 ITT, the Employer shall establish whether it contains a quantifiable deviation or omission in accordance with Sub-clause 22.5 ITT and whether after adding the cost of the deviation to the evaluated tender price it remains the lowest priced tender. If not, then the Employer shall reassess tender ranking in order to establish the lowest evaluated the Tender proposal. |  |  |  |
| В. Qualification Criteria IIT 23.1; In order to be qualified for Contract according to paragraph 23.1 IIT, Tenderer (individually or collectively as JVCA) should demonstrate to the Employer its conformity to requirements of competence, experience, financial health and courts history, specified below:. - Tenderers should comply eligibility requirements, stated in IIT, paragraph 4 (as stated in the Letter of Tender ): - Has no conflict of interest as described in ITT 4.3; - Tenderer was not determined as non-eligible as a result of non-compliance with requirements stated in ITT 4.4; - Documents provided in accordance with Tender Information Sheet in Tender Forms and signed Covenant of Integrity provided by Tenderer - Tenderer has the financial, technical and production capability and capacity required to perform the Contract and Tenderer’s average annual income in the 3 (three) full years (2019, 2020, 2021) was at least 29,4 mil. UAH. In case of tender submitted by JVCA, the leading partner should demonstrate at least 60% compliance with the requirement; Financial capacity confirmation: - Financial information provision according to instructions stated in «Tenderer average annual turnover» form, Provided by Section ІІІ «Tender Forms». - Tenderer must confirm financial means (e.g. liquid assets) availability for Contract fulfillment estimated in sum at least 2,9 mil UAH (Certificate that confirms Tenderer`s financial means (e.g. liquid assets) availability and filled «Financial means», provided in Section ІІІ «Tender Forms»). Technical and production capacity confirmation: - Tenderer shall provide information according to Contractor`s equipment form (Section ІІІ «Tender Forms»). - Tenderer shall provide information about staff according to Contractor`s Staff form and Proposed staff CVs (Section ІІІ «Tender Forms»). - Tenderer has satisfactorily executed similar works to customers, which were fully and successfully and executed, at least, three (3) similar contracts during any of 2019, 2020, 2021, 2022, 2023 years, for the total amount minimum 14,6 mil UAH. Confirmation: Tenderer shall provide information according to «Experience» form with data required in it, provided by Section ІІІ «Tender Forms».. |
|  |  |  | - Tenderer or its agent can undertake guarantee obligations. - The Tenderer (each partner of JVCA) is not bankrupt or under bankruptcy procedures according to the national legislation or regulations. Confirmed via documents provided by authorized official body Tenderer`s registration country, which confirm such fact. |  |  |

Section IІІ. Tender Forms

Table of forms

Letter of Tender	19

Covenant of Integrity	21

Price schedules / WORKS LIST	23

Tender Security Form ……………………………………….…………………………………………………..………………............24

Contractor`s equipment	25

Contractor`s Staff	26

Proposed staff CVs	27

Tenderer Information Sheet 	28

Partner to JVCA Information Sheet	30

Tenderer average annual turnover	32

Financial means 	33

Current Contract Commitments	34

History of Non-Performing Contracts	35

Experience	36

Experience (continuation)	37

Letter of Tender

Note for Tenderers: The Tenderer must prepare the Letter of Tender on stationery with its letterhead clearly showing the Tenderer’s complete name and address. All text within square brackets [ ] is for guidance in preparing this form and shall be deleted by the Tenderer from the final document.

Date:

Tender:

Tot:  _______________________________________________________________________

We, the undersigned, declare that:

- We have examined and have no reservations to the Tender Document, including any amendments to Tender Documents issued in accordance with ITT 8 prior to the deadline for submission of tenders defined in ITT 18.1;

- According to Tender document we offer  execution of following Works:

Construction works on project «Capital repairs of individual heating substations and heating systems in public buildings of Kyiv» Lot 8.1 (11 sites)

_________________________________________________________________________________________

- The total price of our Tender (including VAT) excluding any discounts, offered in item (e) below is:

…………………………………………………………………………………………………………

(in words and numbers)

- Amount of VAT :  ………………………………………………………………………………………………………….

(in words and numbers)

- The discounts offered and the methodology for their application are: ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………

- Our tender shall be valid for the period …….[insert validity period as specified in tender conditions] days from the date fixed for the Tender submission deadline in accordance with the Tender Documents, and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

- If our tender is accepted, we commit to furnish a performance security, in accordance with the Tender Document;

- Our firm, including any subcontractors or suppliers and subsuppliers for any part of the Contract, have nationalities from eligible countries;

- We, including any subcontractors or suppliers and subsuppliers for any part of the Contract have no conflict of interest;

- We are not participating, as a Tenderer or as a subcontractor, in more than one Tender in this Tendering process;

- Our firm, its affiliates or subsidiaries—including any subcontractors or suppliers and subsuppliers for any part of the contract—have not been declared ineligible by the NEFCO and are not under investigation by NEFCO or another international financial institution, under the Purchaser’s country laws or official regulations or by an act of compliance with a decision Європейського Союзу and/or of the United Nations Security Council;

- We are not a government-owned entity / We are a government-owned entity [use one of the two options as appropriate] but we meet the requirement stated in ITT 4.3;

- The following commissions, gratuities, or fees have been paid or are to be paid with respect to the Tendering process or execution of the Contract:

| Name of Recipient | Address | Reason | Amount |
| --- | --- | --- | --- |

(If no one has been paid or is to be paid, indicate “No One.”)

- We understand that this tender, together with your written acceptance thereof included in your notification of award, shall constitute a binding contract between us, until a formal contract is prepared and executed.

- We understand that you are not bound to accept the lowest evaluated tender or any other tender that you may receive.

| Name: |  |
| --- | --- |
| In the capacity of: |  |
| Signed: |  |
| Duly authorised to sign the Tender for and on behalf of: |  |
| Date: |  |

Covenant of Integrity

to [Name of Customer				]

from [Name of Tenderer				]

“We declare and covenant that neither we nor anyone, including any of our directors, employees, agents, joint venture partners or sub-contractors (“the Parties”), where these exist, acting on our behalf with due authority or with our knowledge or consent, or facilitated by us, has engaged, or will engage, in any Prohibited Practices (as defined below) in connection with the tendering process or in the execution or supply of any works, goods or services for [specify the contract or tender invitation] (the “Contract”) and covenant to so inform you if any instance of any such Prohibited Practices shall come to the attention of any person in our organisation having responsibility for ensuring compliance with this Covenant of Integrity (the “Covenant”).

We shall, for the duration of the tender process and, if we are successful in our tender, for the duration of the Contract, appoint and maintain in office an officer, to whom you shall have full and immediate access, having the duty, and the necessary powers, to ensure compliance with this Covenant.

If any of the Parties, where these exist and as applicable, (i) have been convicted in any court of any offence involving  Prohibited Practices in connection with any tendering process or provision of works, goods or services during the five (5) years immediately preceding the date of this Covenant, or (ii) have been dismissed or resigned from any employment on the grounds of being implicated in any Prohibited Practices, or (iii) have been excluded from participation in a tendering procedure on the grounds of Prohibited Practices, or is under investigation, by Nordic Environment Finance Corporation (NEFCO) or by any national or EU institutions or any international financial institution or the United Nations Security Council, we shall give details of any event in (i)-(iii) above together with details of the measures that we have taken, or shall take, to ensure that no Party will commit any Prohibited Practices in connection with the Contract [give details if necessary].

In the event that we are awarded the Contract, we grant the Purchaser/Client/Employer/NEFCO and auditors appointed by any of them, as well as any authority or body having competence under relevant legislation, the right of inspection of our records and those of all our subcontractors under the Contract. We accept to preserve these records generally in accordance with applicable law but in any case for at least six (6) years from the date of performance of the Contract.”

For the purpose of this Covenant, “Prohibited Practices” includes:

• Corrupt Practice meaning the offering, giving, receiving or soliciting, directly or indirectly, anything of value to influence improperly the actions of another party.

• Fraudulent Practice meaning any act or omission, including a misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain a financial or other benefit or to avoid an obligation.

• Coercive Practice meaning impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of any party to influence improperly the actions of a party.

• Collusive Practice meaning an arrangement between two or more parties designed to achieve an improper purpose, including influencing improperly the actions of another party.

• Obstructive Practice meaning (a) deliberately destroying, falsifying, altering or concealing of evidence material to an investigation related to the Contract; and/or threatening, harassing or intimidating any party to prevent it from disclosing its knowledge of matters relevant to such investigation or from pursuing the investigation, or (b) acts intended to materially impede the exercise of NEFCO’s contractual rights of audit or access to information or the rights that any relevant authority has in accordance with any law, regulation or treaty.

• Money Laundering meaning (i) the conversion or transfer of property, knowing that such property is derived from criminal activity or participation in such activity, for the purpose of concealing or disguising the illicit origin of the property or of assisting any person who is involved in such activity to evade the legal consequences of his action;

(ii) the concealment or disguise of the true nature, source, location, disposition, movement, rights with respect to, or ownership of property, knowing that such property is derived from criminal activity or from participation in such activity;

(iii) the acquisition, possession or use of property, knowing, at the time of receipt, that such property was derived from criminal activity or from participation in such activity;

(iv) participation in, association to commit, attempts to commit and aiding, abetting, facilitating and counselling any of the actions mentioned in the foregoing points;

• Financing of terrorism meaning the provision or collection of funds, by any means, directly or indirectly, with the intention that they should be used or in the knowledge that they are to be used, in full or in part, in order to carry out any of the offences within the meaning of Directive (EU) 2017/541 of the European Parliament and of the Council of 15 March 2017 on  combating terrorism and replacing Council Framework Decision 2002/475/JHA and amending Council Framework Decision 2005/671/JHA;

• Theft meaning the misappropriation of property belonging to another party.

Date:

Signature:

[Name and position]

for and on behalf of

[Name of the firm or joint venture]

Price Schedules

Form is provided in separate file, in Ukrainian only

Tender Security Form

Notes for Tenderers: Whole text in square brackets [] provided for help in filling out this form and should be deleted from the final document.

__________________________ [bank name and address of corresponding branch]

Beneficiary:  __________________________ [Customer`s name and address]

Date:  __________________________

TENDER SECURITY №: __________________________

We were informed that: __________________________ [Tenderer`s name] (hereinafter "Tenderer") have provided you with its tender proposal ___________ (hereinafter "Tender proposal") for supplying ________________ [Contract’s name] according to Tender invitation № ___________.

Moreover we understand that according to your terms all Tender proposal must have tender security.

On Tenderer`s request we____________________ [Bank name] hereby commit ourselves compensate you any amount or amounts, which will not exceed  ___________ [amount in numbers] (____________) [amount in words] in total upon receipt your first written claim that states Tenderer`s obligations violation defined by tender terms, due to Tenderer`s:

(a) 	Withdrawal of the Tender proposal during its validity period, stated by Tenderer`s covering letter;

(b) 	Being informed, with acceptance of Tender proposal, by Customer during its validity period (i) did not signed or refused to sign Contract form, if necessary (ii) have not provided or refused to provide Contract security according to Tender document.

This guarantee discontinues: (a) if Tenderer is a winner - upon us receiving Contract copy signed by Tenderer and Security of its fulfillment provided on Tenderers request; (b) if Tenderer is not a winner - on first out of following events: (i) upon us receiving copy of your Tenderer`s Notification of naming of Successful Tenderer; (ii) twenty eight (28) days after expiration date of Tenderer`s tender proposal.

Accordingly: any demand on payments under this guarantee should be received by us in office at or before this date.

This guarantee is regulated by Uniform Rules for Demand Guarantees, ICC Publication No. 758.

_____________________________

[Signature]

Contractor`s equipment

Tenderer must provide adequate information for showing its capability to meet all requirement on main equipment and mechanisms. Separate form must be filled for every position of listed equipment or for alternative equipment proposed by Tenderer. Tenderer must submit provided below information according to its capabilities. Boxes marked with asterisk, (*) shall be used for evaluation.

The following equipment shall be demonstrated by the Tenderer in this form::

- arc welder;

- set of locksmith tools;

- angle grinder;

- power drill;

- Freight vehicle for material transporting

| Equipment type * |  |  |
| --- | --- | --- |
| Equipment information | Manufacturer’s name | Model and power class, Year of manufacture * |
| Current state | Current location |  |
|  | Details on current employment |  |
| Origin | Specify origin of equipment o Owned o Rent o Lease o Custom manufactured |  |

Further information must be provided only for equipment that is not  owned by Tenderer.

| Owner | Owner`s name |  |
| --- | --- | --- |
|  | Owner`s address |  |
|  | Phone number, e-mail | Name and position of contact person |
| Contracts | Details on rent, lease etc. contract which are specific to Project |  |

Tenderer must confirm information provided in table (above) on ownership (or rent) by scanned copies of documents:

- extraction from Tenderer`s balance sheet not earlier than 01.02.2024 which confirms ownership and production capability or valid rental agreement with list of rented equipment and receiving and transmitting act of such equipment or service contract (with list of equipment/vehicles or mechanisms).

If rental agreement is to be considered prolonged for next period, provide appropriate acknowledgement (supplementary agreement or Tenderer`s letter of prolongation for certain period certified by lessor)

Tenderer must demonstrate  presence of  production base and storage spaces and materials storage (specify address and provide description, in case of rent -submit copy of rental agreement) and guarantee continuous and uninterrupted Site providing with appropriate materials and plant according to works schedule.

Contractor`s Staff

Proposed staff

Tenderer must propose qualified staff for requirement compliance for each position listed below:

- Thermal power engineer or specialists with engineering and technical qualifications in thermal power engineering (heat engineering, heating) (minimum 3 years of experience in construction ) at least 1 person;

- Occupational safety and health engineer (minimum 3 years of experience in construction) at least 1 person;

- Expert on adjustment of Instrument hardware, automatic controls and regulation instrumentation management adjuster (adjuster of measuring and control devices and automatics) or an electrician with the appropriate electrical safety group not lower than 3 (provide a copy of the relevant certificates), who has at minimum 3 years of experience in construction at least 1 person;

- Qualified installer of sanitary-technical systems and hardware or a plumber, minimum of 4th grade who has at minimum 3 years of experience in construction - minimum 3 persons;

- Electric welder of manual welding minimum of 4th grade  (submit copy of correspondent permits) (construction, installation and repair and construction works) with minimum 3 years of construction work experience – minimum 1 persons;

- Engineer/foreman/master, employed by the company, which construction work experience (minimum 3 years) and who have worked in the company for minimum 1 year - minimum 1 person.

Info on their experience must be submitted according to below provided forms for each candidate.

| 1. | Title |
| --- | --- |
|  | Name |
| 2. | Title |
|  | Name |
| 3. | Title |
|  | Name |
| etc | Title |
|  | Name |

Proposed staff CVs

Tenderer must submit below mentioned information for each  staff member listed in Section ІІІ (see form “Contractor`s Staff” ). Boxes marked with asterisk (*) shall be used for evaluation.

| Title* |  |  |
| --- | --- | --- |
| Personal data | Name * | Birth date |
|  | Professional qualification |  |
| Workplace | Customer name |  |
|  | Customer address |  |
|  | Phone number | Contact person (head / HR) |
|  | Fax | E-mail |
|  | Title | Working experience, years |

Briefly describe professional experience in reverse chronological order. Specify appropriate for the project exact technical or management experience.

| From* | To* | Company, project, title and corresponding technical and management experience * |
| --- | --- | --- |

Tenderer must submit copies of documents that confirm education of engineering-technical staff members which will be involved in works execution:

Appropriate copies of the documents confirming  education, qualification or special professional training of a staff members which will be involved in works execution (diplomas, certificates, permits etc. that indicate which working qualification was assigned to a staff member of corresponding grade (class, category, group).

Submit notarized copies of documents («according to original» (title signature last name)», which confirms that employees of engineer-technical qualifications and qualified employees  are employed in Tenderer`s enterprise (submit copies of filled first and  last pages of workbook with employment information or copy of employment contract  (in case of employment contract submit employee appointment), note on  acceptance of employment  in form according to decision of  Cabinet of Ministers of Ukraine from 17.062015 № 413 with marking of its acceptance by territorial bodies of State Revenue Service residential register.

Tenderer qualification

Tenderer should provide the information requested in the corresponding Information Sheets included hereunder in order to establish its qualifications to perform the contract in accordance with Section II (Evaluation and Qualification Criteria)

Eligibility

Tenderer Information Sheet

Date: _______________________

Tender No.: _________________

Page ________ of _______ pages

1. Tenderer’s Legal Name: __________________________________________________ EDRPOU code (for Ukrainian tenderers): ____________________________________

2. In the case of a JVCA, the legal name of each partner indicating which partner is the leading one:

3. Tenderer’s actual or intended Country of Constitution, Incorporation, or Registration:

4. Tenderer’s Year of Constitution, Incorporation, or Registration:

5. Tenderer’s Legal Address in Country of Constitution, Incorporation, or Registration:

6. Tenderer’s Authorised Representative Information Name: Address: Telephone/Fax numbers: Email Address:

7. Attached are copies of original documents of: Articles of Incorporation or Registration of firm named in 1, above.

Tenderer must provide:

1. Documents confirming that the Tenderer is not prosecuted  on corruption offence according to legislation on Public Procurement:

- Notification in any form that the Tenderer was not prosecuted  for offence envisaged by paragraph 4 section two of Article 6, paragraph 1 Article «Law of Ukraine «on the Protection of Economic Competition», in form of anti-competitive concerted action in connection with distortion of biddings (tenders);

- Notification must be submitted in form of original letter from Tenderer signed and sealed (if available) by Tenderer , addressed to head of Employer`s tender committee.

2. Documents confirming that:

- The head of the tenderer, which is authorized representing interests during procurement procedure, was not prosecuted for crime connected with procurement procedure offence  or other crime committed with material interest,  from whom  criminal record has been expunged or cleared according to legal procedure

- An extract from the information-analytical system "Accounting of information on bringing a person to criminal responsibility and the presence of a criminal record"(for Ukrainian Tenderers -  provided by structural department of Ministry of internal affairs of Ukraine) dated not preceding the procurement announcement date;

- The head of the tenderer or an individual who is a tenderer has not been brought to liability under the law for a corruption or corruption-related offence

- Information certificate from the Unified State Register of Persons Who Committed Corruption or Corruption Related Offences issued by the National Agency for the Prevention of Corruption not earlier than the date of publication of the procurement announcement on the web portal of the Authorised Body

3. Documents confirming that the Tenderer`s representative is authorized  for conclusion of Contract on procurement: founders' decision report copy, charter copy with contract-conclusion authority, copy of order about appointment of enterprise head, enterprise head`s passport copy or authorized  representative.

4. Original of Power of Attorney for Tenderer`s authorized person to participate  in tendering and to sign documents including upon tendering results in which last name, first name and patronymic  and position of authorized person is stated.

5. Original or notarized copy of notification provided by authorized body (department) (for Ukrainian Tenderers - Public Revenue Service of Ukraine) about absence of debts on taxes and fees payments (mandatory payments) valid on the  tender opening date.

6. If the authorized person or director, or the ultimate beneficial owner, member or participant (shareholder) with a share in the authorized capital of 10 percent or more is a foreign person, namely a citizen of the Russian Federation/Republic of Belarus, provide documents confirming the legal grounds for residence in Ukraine - (passport of a citizen of the former USSR of 1974 with a mark of permanent or temporary residence in Ukraine or a national passport registered in Ukraine, or a certificate of permanent or temporary residence in Ukraine).

7. As part of the proposal, the Tenderer must provide a certificate in any form stating that it does not carry out economic activity or its location (place of residence - for individual entrepreneurs) is not located in the temporarily occupied territory.

If the Tenderer's location is registered in the temporarily occupied territory, the Tenderer must provide confirmation of the change of tax address to another territory of Ukraine issued by an authorised body.

Partner to JVCA Information Sheet

Date: ______________________

Tender No.: ___________________

Page ________ of_ ______ pages

1. Leading Tenderer`s legal name EDRPOU code (for Ukrainian tenderers):

2. JVCA Partner’s Legal Name EDRPOU code (for Ukrainian tenderers):

3. JVCA Partner’s Country of Constitution, Incorporation, or Registration:

4. JVCA Partner’s Year of Constitution into a legally-enforceable JVCA:

5. JVCA Partner’s Legal Address in Country of Constitution, Incorporation, or Registration:

6. JVCA Partner’s Authorized Representative Information Name: Address: Telephone/Fax numbers: Email Address:

7. Attached are copies of original documents of: Articles of Constitution, Incorporation or Registration of firm named in 1, above.

Subcontractors Information Sheet Date: ______________________ Tender No.: ___________________ Page ________ of_ ______ pages Tenderer must submit notification on each economic entity which Tenderer will involve for Works as subcontractor in volume that exceeds 20 % of Contract value using following form: №; Full name of economic entity (subcontractor); EDRPOU code; Location; Types of Works on which subcontractor is planned to be engaged. In cases of subcontractor (subcontractors) engagement, provide copy of Letter of intent with each of them about their obligations to conclude sub-contract on whole period of site construction. In cases subcontractor(s) would not be engaged , provide corresponding statement (notification).

Financial Situation

Tenderer average annual turnover

Tenderer’s Legal Name:  ___________________________  	Date:  _____________________

JVCA Partner Legal Name: _______________________ 	Tender No.:  ________________

Page _______ of _______ pages

| Average annual income* |  |  |
| --- | --- | --- |
| Year | Sum | Currency** |
| 2019 |  |  |
| 2020 |  |  |
| 2021 |  |  |
| ***Average annual income |  |  |

*Tenderers shall attach copies of full financial reports (balance sheets including all related notes and income statements, or justification why such reports can not be provided) for years required above, which:

(а) financial situation of the Tenderer or partner to a JVCA, and not sister or parent companies;

(b) correspond to accounting periods already completed and audited (no statements for partial periods shall be requested or accepted);

(с) audited by respective bodies of the country of the Tenderer in correspondence with requirements of legislation of the Tenderer’s country.

## Ukrainian tenderers should also attach a completed Form “Tax Declaration for Profit Tax” for each year required above certified by a “wet” stamp of respective tax authority.

- ** UAH

*** Average annual income is calculated as total certified payments received for supply in progress or completed, divided by the number of years specified in Section ІІ, Evaluation and Qualification Criteria

Financial means

Specify proposed sources of financing, such as liquid assets, unencumbered real assets, lines of credit and other financial means, net of current commitments, available to meet the total cash flow demands of the subject contract or contracts as indicated in Section II, Evaluation and Qualification Criteria.

| Funding sources | Sum (EURO or national currency equivalent) |
| --- | --- |
| 1. |  |
| 2. |  |
| 3. |  |
| 4. |  |

Current Contract Commitments

Tenderers and each partner to a JVCA should provide information on their current commitments on all contracts that they have been awarded, for which a letter of intent or acceptance has been received, or lastly for contracts approaching completion but for which an unqualified full completion certificate has yet to be issued.

| Name of contract | Employer, contact address, telephone, fax & email | Value of outstanding supply (current Euro equivalent) | Estimated completion date | Average monthly invoicing over last six months (Euro/month) |
| --- | --- | --- | --- | --- |
| 1. |  |  |  |  |
| 2. |  |  |  |  |
| 3. |  |  |  |  |
| 4. |  |  |  |  |
| 5. |  |  |  |  |
| etc. |  |  |  |  |

History of Non-Performing Contracts

Tenderer’s Legal Name:  ___________________________     	Date:  ___________________

JVCA Partner’s Legal Name:  _______________________	   ___________________

Tender No.:  __________________	Page ______ of _______ pages

| Non-Performing Contracts in accordance with Section III, Evaluation Criteria |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contract non-performance did not occur during the stipulated period, in accordance with Sub-Clause 26.1(b) of Section III, Evaluation Criteria |  |  |  |  |  |
| Year | Non-performed portion of contract |  | Contract identification | Total Contract amount (current value, Euro equivalent) |  |
| Pending Litigation, in accordance with Section III, Evaluation Criteria |  |  |  |  |  |
| No pending litigation Pending litigation, as indicated below |  |  |  |  |  |
| Year |  | Outcome as Percent of Total Assets | Contract Identification |  | Total Contract Amount (current value, Euro equivalent) |
|  |  |  | Contract Identification: Name of Employer: Address of Employer: Matter in dispute: |  |  |
|  |  |  | Contract Identification: Name of Employer: Address of Employer: Matter in dispute: |  |  |

Experience

Tenderer shall proof experience of execution of similar works for any of the years 2019, 2020, 2021, 2022, 2023. One site (facility) can contain several heating substations, or boilers or heating systems.

Similar agreements should be considered to be those confirming the fact of the following works execution:

- Capital repair, or modernization, or installation/reconstruction, or technical re-equipment of individual heating  substations (IHSs) or boiler rooms, separately or as a part of other general works including the installation of remote monitoring and data acquisition systems for heat generating and/or heat distribution equipment separately or as part of other general works (at least 10 IHSs);

- Capital repair or modernization or installation, or reconstruction of heating systems, or internal heat supply systems (minimum 2 sites);

Tenderer’s Legal Name:  ___________________________     	Date:  _____________________

JVCA Partner’s Legal Name: _________________________	 Tender No.:  __________________

Page _______ of _______ pages

| Equivalent Contract* No. [insert specific number] of [total number of contracts] required | Information |  |  |
| --- | --- | --- | --- |
| Contract Identification |  |  |  |
| Award date Completion date |  |  |  |
| Role in Contract |  |  |  |
| Total Contract amount |  |  | UAH |
| If a partner in a JVCA, specify participation proportion in total contract amount | _________% | UAH ______ |  |
| Customer’s Name: |  |  |  |
| Actual Customer’s contact data: Address: Telephone/fax number: E-mail: Contract person: |  |  |  |

* Tenderers should submit copies of the signed similar contract  stated in the Form, as well as certificates of accepted works  in accordance with form kb-2v (or in other format)

Experience (continuation)

Tenderer’s Legal Name:  ___________________________     	Page _______ of _______ pages

JVCA Partner’s Legal Name:  ___________________________

| Equivalent Contract No. [insert specific number] of [total number of contracts] required | Information |
| --- | --- |
| Description of the equivalency: |  |
| Amount |  |
| Physical size |  |
| Complexity |  |
| Technology |  |

Tenderer must submit copies of reference letters (minimum three) from customers (counterparties) about collaboration with Tenderer on execution of similar works in full scope, on terms,  quality and in time frames envisaged by submitted copies of similar contracts.

Section ІV. Employer`s Requirements

Available in Ukrainian only

Технічні  вимоги  Замовника

на виконання будівельних робіт з капітального ремонту індивідуальних теплових пунктів та систем опалення у громадських будівлях м. Києва

Lot 8.1

Перелік об’єктів

До переліку входить 11 об’єктів м. Києва з яких на 2-х об’єктах будуть виконуватися роботи з капітального ремонту систем опалення (СО) та на 9-ти об’єктів на яких будуть виконуватися роботи з капітального ремонту індивідуальних теплових пунктів (ІТП).

| № | Назва об’єкту | Адреса | Вид робіт |
| --- | --- | --- | --- |
| 1 | Дошкільний навчальний заклад (дитячий садок) компенсуючого типу, спеціального, №611 Оболонського району м.Києва | проспект Оболонський, будинок 37-Б | СО |
| 2 | Дошкільний навчальний заклад компенсуючого типу (санаторний) № 163 Подільського району м. Києва | вулиця Копилівська, будинок 55 | СО |
| 3 | ШКОЛА І-ІІІ СТУПЕНІВ №285 ОБОЛОНСЬКОГО РАЙОНУ М.КИЄВА | ВУЛИЦЯ ПОЛЯРНА, будинок 8-В | ІТП |
| 4 | ДОШКІЛЬНИЙ НАВЧАЛЬНИЙ ЗАКЛАД (ЯСЛА-САДОК) № 668 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ПРОСПЕКТ ВОЛОДИМИРА ІВАСЮКА, БУДИНОК 35 -А | ІТП |
| 5 | ДОШКІЛЬНИЙ НАВЧАЛЬНИЙ ЗАКЛАД (ЯСЛА-САДОК) КОМБІНОВАНОГО ТИПУ № 673 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ВУЛИЦЯ ПРИРІЧНА, будинок 17-Б | ІТП |
| 6 | ДОШКІЛЬНИЙ НАВЧАЛЬНИЙ ЗАКЛАД (ЯСЛА-САДОК) № 685 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ВУЛИЦЯ ПРИОЗЕРНА, будинок 6 | ІТП |
| 7 | ДОШКІЛЬНИЙ НАВЧАЛЬНИЙ ЗАКЛАД (ЯСЛА-САДОК) № 804 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ВУЛИЦЯ БЕРЕЖАНСЬКА, 14-А | ІТП |
| 8 | ШКОЛА І-ІІІ СТУПЕНІВ № 8 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ВУЛИЦЯ ВИШГОРОДСЬКА, будинок 6 | ІТП |
| 9 | ШКОЛА І-ІІІ СТУПЕНІВ № 245 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ВУЛИЦЯ ПІВНІЧНА, 26 | ІТП |
| 10 | ШКОЛА I СТУПЕНЯ №268 ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ПРОСПЕКТ ВОЛОДИМИРА ІВАСЮКА,43А (ПРОСПЕКТ ГЕРОЇВ СТАЛІНГРАДА, БУДИНОК 43-А) | ІТП |
| 11 | СПЕЦІАЛІЗОВАНА ШКОЛА №252 ІМЕНІ ВАСИЛЯ СИМОНЕНКА ОБОЛОНСЬКОГО РАЙОНУ М. КИЄВА | ВУЛИЦЯ ЗОЇ ГАЙДАЙ, будинок 10-В | ІТП |

I. Технічне завдання

на виконання будівельних робіт з капітального ремонту

індивідуальних теплових пунктів в громадських будівлях м. Києва

Метою виконання робіт з капітального ремонту та відновлення працездатності ІТП є забезпечення економії енергетичних ресурсів на об’єкті шляхом:

1) Відновлення працездатності автоматики ІТП;

2) Постійного контролю за параметрами роботи індивідуального теплового пункту, вузлів обліку енергоресурсів та води, а також температур всередині приміщення;

3) Балансування внутрішньої системи опалення та виконання промивки системи;

4) Виконання налаштування індивідуального теплового пункту та системи опалення для забезпечення оптимально необхідного споживання енергоресурсів.

- Існуюча ситуація

У  будівлі закладів бюджетної сфери встановленні індивідуальні теплові пункти, що, як правило, забезпечують:

- 	регулювання теплоспоживання на потреби опалення в залежності від зовнішньої температури;

- 	регулювання теплоспоживання на потреби опалення в залежності від часу доби та дня тижня;

- 	регулювання теплоспоживання на потреби гарячого водопостачання в залежності від фактичних витрат води, часу доби та дня тижня;

- 	облік холодної води, що йде на приготування гарячої води.

Через значний термін експлуатації частина складових теплопункту вийшла з ладу, що не дозволяє проводити ефективне регулювання теплоспоживання та призводить до перевитрат теплової енергії. Окрім того, збої в роботі системи опалення призводять до необхідності використовувати електропідігрівачі, що додатково призводить до збільшення витрат на електричну енергію.

Контроль за температурою всередині приміщення не ведеться, що ускладнює проведення налаштування обладнання та балансування системи опалення.

Знімання даних з вузлів обліку проводиться, як правило, вручну 1 раз на місяць (в ряді випадків 2 рази на тиждень), що унеможливлює проведення запобіжних дій по налаштуванню обладнання.

  - Модульні індивідуальні теплові пункти (МІТП)

МІТП оснащені автоматичними програмованими контролерами, що, як правило, не мають інтерфейсних виходів для підключення до системи диспетчеризації.

Регулювання з погодною корекцією відбувається згідно показників давачів температури зовнішнього повітря та температури подачі теплоносія в систему  опалення будівлі - Т11. А також, до системи гарячого водопостачання (ГВП) - згідно показників давачів температури – Т3.

Регулюючі елементи – клапани з електроприводами з 3-точковим сигналом управління або з сигналом управління 2-10 В.

Циркуляція теплоносія в системі опалення будівлі забезпечується за рахунок спарених циркуляційних насосів з мокрим ротором. Передбачений захист від зниження тиску в системі опалення – реле тиску.

Лічильник води на потреби гарячого водопостачання механічного типу, без імпульсних або інших виходів, що унеможливлює їх диспетчеризацію.

Серед основних несправностей:

- вихід з ладу контролера;

- вихід з ладу електроприводів регуляторів;

- вихід з ладу регулюючих клапанів;

- вихід з ладу насосів;

- вихід з ладу давачів температури.

  - Лічильники теплової енергії.

Лічильники теплової енергії, що встановлені в будівлях, як правило, мають інтерфейсний вихід (RS-232) та дозволяють отримувати інформацію про миттєве, погодинне та подобове теплоспоживання, температуру та витрати теплоносія в подавальному та зворотному трубопроводах.

  - Лічильники обліку води.

У системі холодного водопостачання будівлі, як правило, встановлені лічильники механічного типу, що не мають імпульсних або інтерфейсних виходів.

  - Лічильники обліку електроенергії.

Для обліку електричної енергії встановлені лічильники різних типів, частина яких має інтерфейсні та/або імпульсні виходи.

  - Електропостачання

Приміщення теплопунктів, як правило, мають тільки систему освітлення, а також-живлення теплового пункту та теплолічильника. Щитові, в більшості випадків, знаходяться на

І-му  поверсі будинку та мають електричні вводи U = ~380 В,  H = 50 Гц.

  - Система опалення

Система опалення будівлі, як правило однотрубна. Частина запірної арматури знаходиться в неробочому стані. Теплова ізоляція пошкоджена або відсутня. Внутрішня система опалення потребує промивки та балансування.

- Роботи, які необхідно врахувати при виконанні капітального ремонту індивідуальних теплових пунктів.

Усі застосовані матеріали та обладнання, а також технічні рішення повинні забезпечувати максимальну ефективність та енергозбереження, а також відповідати вимогам діючих нормативних документів для даного типу закладів.

Загальний перелік будівельних робіт, який можливий при проведенні капітального ремонту індивідуальних теплових пунктів, в громадських будівлях м. Києва наведений нижче:

- Заміна електроприводу клапана системи опалення (в разі необхідності)

- Заміна/встановлення електроприводу клапана системи ГВП (в разі необхідності)

- Заміна клапану опалення (в разі необхідності)

- Заміна клапану ГВП (в разі необхідності)

- Заміна лічильника холодного водопостачання на лічильник з імпульсним виходом

- Заміна лічильника води на ГВП на лічильник з імпульсним виходом

- Заміна (встановлення) зовнішнього давача температури (в разі необхідності)

- Заміна давача температури на подачі теплоносія в систему опалення будівлі (в разі необхідності)

- Заміна давача температури на подачі в систему ГВП (в разі необхідності)

- Встановлення давачів температури на зворотних трубопроводах в теплопункті

- Встановлення давачів температури всередині приміщення (не менше 3-х)

- Встановлення давача руху в приміщенні теплового пункту

- Встановлення поплавкового сигналізатору рівня в приміщенні теплового пункту

- Заміна контролера ІТП (в разі необхідності) на такий, що може бути підключений до системи диспетчеризації та мати можливість дистанційного керування

- Підключення обладнання ІТП (електроприводів регуляторів системи опалення та ГВП, насосів, давачів та ін.) до контролера

- Встановлення щита збору та передачі даних

- Встановлення GSM – модему

- Підключення щита збору даних до мережі інтернет

- Підключення щита збору даних до теплолічильника

- Підключення щита збору даних до водолічильників (загальний ввід в будівлю - комерційний облік та води на ГВП - технічний облік)

- Підключення щита збору даних до електролічильника

- Підключення щита збору даних до контролера теплового пункту

- Прокладання кабелю в лотках або в гофрорукаві.

- Розробка програмного модулю для щита збору та передачі даних

- Пусконалогоджувальні роботи Системи дистанційного контролю

- Встановлення та налаштування програмного забезпечення на об’єкті

- Підключення контролера ІТП до системи дистанційного контролю

- Встановлення балансувальних клапанів (за необхідності)

- Регулювання (балансування) системи опалення будівлі

- Промивка МІТП, грязьовиків та фільтрів загальної системи теплопостачання

- Заміна циркуляційних насосів системи опалення (в разі необхідності)

- Заміна (встановлення) циркуляційних насосів системи гарячого водопостачання (в разі необхідності)

- Заміна дренажного насосу (в разі необхідності)

- Облаштування лінії циркуляції ГВП в межах теплового пункту (у разі відсутності лінії циркуляції в будівлі)

- Встановлення на ІТП контрольно-вимірювальних приладів (манометрів та термометрів) у необхідній кількості

- Пусконалагоджувальні роботи індивідуального теплового пункту

- Відновлення теплової ізоляції трубопроводів

- В разі необхідності, перерахунок обмежуючих пристроїв (дросельних діафрагм) та їх заміна

- Введення відремонтованого обладнання теплового пункту та системи диспетчеризації в експлуатацію

- Навчання персоналу

Детальний перелік об’єму робіт на матеріалів для кожного об’єкту наданий в Розділі IІІ. Форми Тендерних пропозицій -  Форма Прейскуранту. За погодженням із Замовником при виконанні контракту зазначений перелік може бути доповнений та/або змінений.

Всі посилання в прейскуранті на конкретну торговельну марку чи фірму, джерело походження матеріалів або виробника, вважати індикативною інформацією. Учасник може запропонувати матеріали і обладнання інших виробників, які мають такі ж, або кращі, характеристики.

## 2.1. Загальні технічні вимоги

2.1.1 Учасник повинен надати документи, що підтверджують відповідність Учасника  технічним  вимогам виконання робіт:

Копія діючої протягом повного періоду виконання робіт ліцензії на право здійснення відповідного виду діяльності (господарська діяльність, пов’язана із створенням об’єктів архітектури/господарська діяльність з будівництва об’єктів) та копію додатку до неї (перелік робіт провадження господарської діяльності), де обов’язково наявна інформація про категорію складності не нижче ІIІ та/або клас наслідків (відповідальності) об’єктів будівництва – не нижче класу СС2 - незначні наслідки з обов’язковою наявністю таких робіт:

- монтаж технологічного устаткування;

- виконання пусконалагоджувальних робіт (визначається ліцензіатом за видами технологічного устаткування);

- монтаж внутрішніх інженерних мереж, систем, приладів і засобів вимірювання, водопроводу та каналізації, опалення, технологічних трубопроводів, технологічних систем, електропостачання, електрообладнання і електроосвітлення, автоматизації і контрольно-вимірювальних приладів.

У разі залучення субпідрядника – надати  копію діючої протягом повного періоду виконання робіт ліцензії субпідрядника та копію додатку до неї, (перелік робіт провадження господарської діяльності, які буде виконувати субпідрядник та які підлягають ліцензуванню).

Виконавець несе повну відповідальність щодо дотримання норм та правил з охорони праці та техніки безпеки під час виконання робіт та отримання всіх необхідних дозволів, ліцензій, декларацій (в тому числі на виконання зварювальних робіт), сертифікатів, повідомлень, тощо.

2.1.2 Виконавець повинен підібрати основне та додаткове обладнання і матеріали відповідно до проектної документації. Проектна документація надається Замовником учаснику тендеру за вимогою, що складається у довільній формі.

2.1.3 Технологічні компоненти ІТП повинні бути серійного виробництва, мати якість, що відповідає вимогам міжнародних стандартів, бути атестованими в Державному Комітеті України із стандартизації згідно з законодавством України. Все енергоспоживаюче обладнання повинне бути атестоване як високоефективне.

2.1.4 Всі виконані роботи та надані матеріали повинні відповідати українським та міжнародним правилам і нормативам проектування та стандартам безпеки, ДБН В.2.5-39:2008

«Теплові мережі» тощо.

Роботи повинні виконуватись з дотриманням ДСТУ (ГОСТ), ДБН, Правил користування тепловою енергією, Правил електро- та пожежної безпеки, Охорони праці та інших нормативних документів, що діють на території України.

- Вимоги до капітального ремонту індивідуальних теплових пунктів

3.1 Всі рішення щодо капітального ремонту теплопунктів приймаються Виконавцем з урахуванням вимог цього документу, технічних характеристик об’єктів, досвіду експлуатації та обслуговування обладнання, а також надійної і тривалої його роботи, та погоджуються з Замовником. Все обладнання та матеріали встановлюються у відповідності до інструкцій та рекомендацій виробника.

3.2 ІТП повинні мати естетичний вигляд, легкість обслуговування та зручність читання показників контрольно-вимірювальних приладів. Необхідно забезпечити можливість обслуговування кожного модулю з однієї сторони (або двох суміжних).

3.3 Необхідно також забезпечити можливість опломбування всієї запірної арматури (заглушок) на подавальному та зворотному трубопроводах тепломережі, та фланцевих з’єднань (отвори в болтах) під дросельні діафрагми контуру опалення та гарячого водопостачання.

3.4 Модулі ГВП забезпечуються циркуляційною лінією. В разі неможливості відновлення існуючої циркуляційної лінії – необхідно передбачити її монтаж в межах теплопункту, із встановленням циркуляційного насосу.

3.5  В разі припинення електропостачання:

а) регулюючий клапан модулю системи опалення повинен залишитись в проміжному положенні, або повернутися в  проміжне положення (за наявності зворотного механізму)  для забезпечення мінімального протоку теплоносія в систему опалення будівлі для захисту її від замерзання;

б) регулюючий клапан модулю системи гарячого водопостачання повинен повернутися в «закрите» положення для захисту теплообмінника від закипання.

3.6 Після відновлення електропостачання система автоматичного регулювання та управління повинна забезпечити вмикання насосів та відновлення роботи модулів без втручання експлуатаційного персоналу.

3.7 Сучасний контролер ІТП повинен забезпечити можливість:

- пропорційного коригування значень температури теплоносія в системі опалення (трубопровід Т11) відповідно до температури зовнішнього повітря (погодне регулювання);

- зв’язку з комп’ютером за допомогою стандартного інтерфейсу (RS-232, 485) для дистанційного керування.;

Заміна щита автоматики на щит автоматики та диспетчеризації з наступними функціями:

- захист мереж від струмів короткого замикання;

- перемикання насосів (основного і резервного) згідно заданої програми. Автоматичне включення резерву;

- насос системи опалення вимикається, коли тиск буде нижче встановленого для контактного манометра;

- можливість ручного вмикання–вимикання насосів;

- автоматичне вмикання насосів після перерви в електропостачанні;

- автоматичне відключення циркуляційного насосу ГВП у разі падіння тиску на вході насосу нижче встановленого для контактного манометра;

- збір інформації від контролера системи опалення;

- збір інформації від лічильника теплової енергії;

- збір інформації від лічильників холодної води;

- збір інформації від лічильників електроенергії;

- збір інформації від термометрів в приміщенні;

- збір аварійної інформації від обладнання теплового пункту;

- передача зібраної інформації через GSM зв'язок та за допомогою мережі Internet.

3.8 Блоки регулювання та управління повинні бути захищені від несанкціонованого доступу.

3.9 Усі індивідуальні теплопункти повинні пройти іспити під навантаженням відповідно до  діючих нормативів України.

3.10 Виконавець має передбачити налагоджування автоматики таким чином, щоб забезпечувалась функція зниження температури в неробочий час без порушення умов комфортності в приміщеннях в робочі години.

## Інші вимоги

3.11.1 Допоміжне обладнання і пристосування.

Для ефективного функціонування і технічного обслуговування, теплопункт повинен бути укомплектований всім необхідним допоміжним обладнанням і пристосуваннями.

В допоміжне обладнання необхідно включити комплект табличок, виконаних із жесті розміром 100х80 мм, з нумерацією фарбою під трафарет (згідно принципової схеми теплопункту), для наступного встановлення на елементах модулів.

На всіх відгалуженнях ІТП необхідно виконати розмітку та маркування трубопроводів у відповідності до їх призначення та згідно діючих ДБН.

На обладнанні необхідно передбачити місце (кишеню) для паспортів, технічної та експлуатаційної документації.

3.11.2 Паспорти, інструкції та посібники.

ІТП (або кожний модуль) повинен мати технічний паспорт. Усі матеріали, частини, обладнання і компоненти збірної конструкції в цілому і ті, що постачаються окремо, повинні супроводжуватися паспортами, стандартними і спеціальними інструкціями з установки та експлуатації, як це вимагає існуюча виробнича практика. Інструкції з експлуатації повинні надаватися в двох примірниках. Повинні бути представлені також характеристики матеріалів, що визначають безпечне поводження з ними. Повинна застосовуватись метрична система мір.

Інструкції з експлуатації модулів та інша технічна документація повинні бути українською мовою. Інструкції повинні включати сертифікати та акти у відповідності нормативним вимогам України до систем теплопостачання та теплоспоживання, трубопроводів гарячої води, обладнання, що працює під тиском, електричного обладнання.

3.11.3 Вимоги по технічному обслуговуванню та ремонту.

Теплопункт, разом із всім обладнанням, повинен вимагати тільки звичайного технічного обслуговування і сезонних оглядів. Вимоги у відношенні технічного обслуговування, такого як чищення, промивання, регулювання і змащення обладнання та ін., повинні бути заздалегідь визначені в технічному паспорті модуля та в інструкціях по експлуатації комплектуючого обладнання.

3.11.4 Гарантійні зобов'язання.

Якість виконаних робіт повинна гарантуватися за Договором щонайменше впродовж  2  років з дня вводу його в постійну експлуатацію.

Термін гарантії на обладнання, що встановлене при проведенні капітального ремонту індивідуальних теплових пунктів (ІТП) – згідно гарантії виробника обладнання, зазначеної у Паспорті (гарантійному талоні) обладнання.

3.11.5 Виконавець також зобов’язується:

(а) власними силами передати балансоутримувачу об’єкта все демонтоване обладнання та матеріали за Актами прийому-передачі та повідомити про це Замовника протягом 5 (п’яти) робочих днів з моменту їх демонтажу.

(б) звільнити Об'єкт від техніки, невикористаних матеріалів, будівельного сміття після закінчення виконання Робіт протягом 7 (семи) календарних днів з моменту завершення Робіт;

(г) Нести відповідальність за збереження матеріальних цінностей на Об’єкті, освітлення й огородження його, дотримання санітарних і протипожежних вимог, складування будівельних матеріалів і техніки, охорону праці й техніку безпеки при проведенні робіт в умовах щільної житлової забудови та інших правил, що застосовуються при здійсненні ремонтно-будівельних робіт;

(д) забезпечувати замовлення, постачання, приймання, розвантаження, складування, зберігання, подавання на будівельний майданчик матеріалів, конструкцій та обладнання, контроль якості, кількості та комплектності постачання цих ресурсів

## Екологічні вимоги

3.12 Демонтовані матеріали та обладнання, що не підлягають повторному використанню, а також будівельні відходи та сміття повинні вивозитись і утилізовуватись у відповідності до вимог українського законодавства.

3.13 Не допускається використання матеріалів, що містять азбест.

3.14. Азбестові відходи розглядаються в Україні як небезпечні відходи. Наказ міністерства охорони здоров'я №762 від 10.01.2012 «Про затвердження Державних санітарних норм і правил Про безпеку і захист працівників від шкідливого впливу азбесту і азбестовмісних матеріалів», містить конкретні положення по роботах та обробці таких матеріалів.

Це означає, що проведення ремонтних робіт можливе тільки після демонтажу азбесту, особливо азбестоцементного брухту та азбестової крихти які розглядаються як промислові небезпечні відходи IV класу які в подальшому піддають конкретному кваліфікованому поводженню. Це означає, що при виявленні необхідності демонтажу виробів з азбестових матеріалів, підрядник зобов'язаний залучити спеціалізовану компанію або мати ліцензію на роботи з матеріалами, що містять азбест: збір, зберігання, транспортування, очищення, прибирання та захоронення відповідно до Закону України "Про забезпечення санітарного та епідемічного добробуту населення" Стаття 13 Ліцензування господарської діяльності, пов'язаної з потенційною небезпекою для здоров'я людини. Види господарської діяльності, пов'язані з потенційною небезпекою для здоров'я людини, підлягають ліцензуванню у випадках, встановлених законом. Ліцензійні умови щодо видів господарської діяльності, які пов'язані з потенційною небезпекою для здоров'я людини, обов'язково включають вимоги щодо забезпечення санітарного та епідеміологічного благополуччя населення.

# 4. Вимоги до обладнання

## 4.1. Капітальний ремонт ІТП

Нижче надається приблизна схема ІТП. Для кожного об’єкту розроблена проектна документація з відповідними рішеннями.

Рис. Схема індивідуального теплового пункту.

Основна технічна специфікація ІТП.

(Номери позицій у відповідності до принципової схеми)

| Позиція № 1 Щит електричний розподільчий |  | Щит електричний розподільчий забезпечує живленням все обладнання ІТП. Встановлення повинно відповідати наступним вимогам: - Нормативним документам, що діють на території України; - Повинен бути забезпечений стандарт захисту не гірший IP 54. |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Установка повинна мати: - аварійні вимикачі насосів у відповідності до вимог виробника насосів; - контактори з регульованим захистом від теплового перевантаження у відповідності вимогам виробника насосів; - панель запобіжників. |  |  |  |
| Позиція №2 Блок регулювання системи опалення та ГВП (Контролер ІТП) |  | Контролери у позиціях 2, 2.2, 2.3 можуть інтегруватися в один або більше блоків при умові, що їх функціональні характеристики залишаться такими ж самими. Регулювання – пропорційне. |  |  |  |
|  |  | Контролер забезпечує: - Пропорційне корегування значень температури теплоносія в системі опалення (трубопровід Т11) відповідно температурі зовнішнього повітря (погодне регулювання); |  |  |  |
|  |  | - Можливість зв’язку з комп’ютером за допомогою стандартного інтерфейсу (RS-232, 485). Дозволяється використовувати напругу живлення 220В, при цьому необхідно забезпечити стандарт захисту не гірший IP 54 |  |  |  |
|  |  | Контролер може бути підключений до системи диспетчеризації та мати можливість дистанційного керування |  |  |  |
| Позиція №2.2 Блок управління насосами системи опалення. |  | Забезпечує управління насосом, з заданими функціями: |  |  |  |
|  |  | - Забезпечує перемикання насосів (основного і резервного) згідно заданої програми. Автоматичне включення резерву. |  |  |  |
|  |  | - Насос системи опалення повинен відключитися, коли тиск буде нижче встановленого для контактного манометра (поз. Р1.1). |  |  |  |
|  |  | - Можливість ручного вмикання – вимикання насосів. |  |  |  |
|  |  | - Автоматичне вмикання насосів після перерви в електропостачанні. |  |  |  |
|  |  | Повинен бути забезпечений стандарт захисту не гірший IP 54. |  |  |  |
|  |  | Управління роботою насосу може також забезпечуватися електронною системою насосу або контролером ІТП. |  |  |  |
| Позиція №2.3 Блок управління насосом системи ГВП. |  | Забезпечує управління насосом із заданими функціями: |  |  |  |
|  |  | - Автоматичне відключення циркуляційного насосу ГВП у разі падіння тиску на вході насосу нижче встановленого для контактного манометра (поз. Р1.2). |  |  |  |
|  |  | Можливість ручного вмикання – вимикання насосу. |  |  |  |
|  |  | Автоматичне вмикання насосу після перерви в електропостачанні. |  |  |  |
|  |  | Вимикання насосу в разі перевищення температури теплоносія в циркуляційному трубопроводі заданої вставки. |  |  |  |
|  |  | Повинен бути забезпечений стандарт захисту не гірший IP 54. |  |  |  |
|  |  | Управління роботою насосу може також забезпечуватися електронною системою насосу. |  |  |  |
| Позиція №3, 3.1 |  | Датчик температури води |  |  |  |
| Датчик температури | Діапазон вимірювання |  | 0 °C ÷ 100 °C |  |  |
| Позиція №4 | Датчик температури зовнішнього повітря |  |  |  |  |
| Датчик температури | Діапазон вимірювання |  | -30 °C ÷ +50 °C |  |  |
| Позиція № 5 | Робочий тиск |  |  | 1,6 МПа |  |
| Клапан регулюючий системи опалення | Безпечна робоча температура |  |  | 150 °C |  |
|  | З'єднання |  |  | Фланцеве або різьбове |  |
| Позиція № 5.1 | Привід регулюючого клапану – лінійного типу, напруга живлення приводу менше 37,5 В; управління по сигналу від блоку управління (поз. 2). |  |  |  |  |
| Привід клапану системи опалення | Дозволяється використовувати напругу живлення 220В, при цьому необхідно забезпечити стандарт захисту не гірший IP 54 (частковий захист від проникнення пилу, та захист від води розпиленої з будь - якого напряму). |  |  |  |  |
|  | Час спрацювання від «зачинено» до «відчинено» - до 150 сек. Можливість ручного керування. Встановлення в проміжному положенні у разі відключення електропостачання. |  |  |  |  |
| Позиція № 6 | Клапан регулюючий температури системи гарячого водопостачання. |  |  |  |  |
| Клапан регулюючий системи ГВП | Забезпечує підтримування температури води в подавальному трубопроводі ГВП на потрібному рівні (необхідний діапазон +35°C ÷ +60°C). Регулятор температури системи гарячого водопостачання може бути як прямої дії, так і з електроприводом та контролером |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа |  |
|  | Безпечна робоча температура |  |  | 150 °C |  |
|  | З'єднання |  |  | Фланцеве або різьбове |  |
| Позиція № 6.1 Привід клапану системи гарячого водопостачання (ГВП) | Привід – лінійного типу ((поз. 2.1). Напруга живлення приводу менше 37,5 В; управління по сигналу від блоку управління (поз. 2). |  |  |  |  |
|  | Дозволяється використовувати напругу живлення 220В, при цьому необхідно забезпечити стандарт захисту не гірший IP 54 (частковий захист від проникнення пилу, та захист від води розпиленої з будь - якого напряму). |  |  |  |  |
|  | В разі припинення електропостачання - повинен повернутися в "закрите" положення для захисту теплообмінника від закипання. Час спрацювання - до 35 сек. Можливість ручного керування. |  |  |  |  |
| Позиція № 7, 7.1 | Регулюючий клапан перепаду тиску, що забезпечує: постійну різницю тиску між подавальним трубопроводом тепломережі (перед регулюючим клапаном системи опалення, системи ГВП) та зворотним трубопроводом; неточність утримання тиску не більше ± 2,5 % від встановленого значення. Сигнальні трубки, що з'єднуються з регулятором повинні обладнуватися запірними (кульовими) кранами. Сигнальні трубки повинні з’єднуватись з трубопроводами зверху з метою запобігання їх забруднення. |  |  |  |  |
| Регулятор постійності перепаду тиску |  |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа |  |
|  | Безпечна робоча температура |  |  | 150 °C |  |
|  | З'єднання |  |  | Фланцеве або різьбове |  |
| Позиція № 8 Насос циркуляційний системи опалення | Циркуляційний насос з мокрим ротором. При обґрунтуванні - дозволяється використання здвоєного циркуляційного насосу. Насос встановлюється у відповідності з інструкціями виробника. Необхідно забезпечити можливість обслуговування та демонтажу насосу без розбирання трубопроводів та інших компонентів. Робочий тиск насосу у відповідності до розрахункового гідравлічного опору внутрішньої системи опалення будинку, з урахуванням гідравлічних опорів елементів модулю. Рівень шуму не більше 40 dB. |  |  |  |  |
|  | Робочий тиск |  |  | 1,0 МПа |  |
|  | Безпечна робоча температура |  |  | 110 °C |  |
|  | З'єднання |  |  | Фланцеве |  |
|  | Електроживлення: ~ 220/380В, 50 Гц. |  |  |  |  |
| Позиція № 9 Обчислювач теплолічильника | Забезпечує вимірювання теплової енергії, об’ємної, масової витрати та температури теплоносія в подавальному та зворотному трубопроводах на загальному тепловому вводі в будівлю. Прилад обліку повинен відповідати класу точності (не гірше) 3 згідно Постанови кабінету міністрів України «Технічний регламент щодо суттєвих вимог до засобів вимірювальної техніки» від 08.04.2009р. № 332, та класу точності (не гірше) 2, згідно ДСТУ EN 1434-1:2006. Прилад обліку повинен забезпечувати можливість зв’язку з комп’ютером за допомогою інтерфейсного виходу (RS-232) та бути підключений до системи диспетчеризації. |  |  |  |  |
| Позиція № 9.1 | Механічний водолічильник для некомерційного обліку на трубопроводі холодної води у системі ГВП з імпульсним виходом. Повинен мати можливість підключення до системи диспетчеризації. |  |  |  |  |
| Водолічильник | З'єднання |  |  |  | Фланцеве або різьбове |
| Позиція № 10,10.1 | Сітчастий фільтр. Можливість проведення чищення без демонтажу. В кришці фільтру встановити штуцер з запірним кульовим краном та заглушкою, для швидкого промивання без розбирання. |  |  |  |  |
| Фільтр з промивним штуцером | Розмір чарунки сітки фільтру: 0,4 ÷ 0,7 мм. |  |  |  |  |
|  | Повинна додаватися 1 запасна сітка. |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа |  |
|  | Безпечна робоча температура |  |  | 150 °C |  |
|  | Матеріал |  |  | Бронзовий або латунний. Для Ду ≥ 50 мм дозволяється використовувати сталевий корпус з забезпеченням захисту від конденсації зовні |  |
|  | З'єднання |  |  | Фланцеве або різьбове |  |
| Позиція № 11, 11.1 | Фланцеве з'єднання для встановлення дросельної діафрагми. |  |  |  |  |
| Фланці | Встановлюється в разі необхідності |  |  |  |  |
| Позиція № 12 | Запірний клапан кульового типу |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа |  |
| Клапан запірний ручний кульовий | Безпечна робоча температура |  |  | 150 °C |  |
|  | З'єднання |  |  | Фланцеве |  |
| Позиція № 12.1 | Робочий тиск |  |  | 1,6 МПа |  |
| Клапан запірний ручний кульовий | Безпечна робоча температура |  |  | 100°C |  |
|  | З'єднання |  |  | Фланцеве |  |
| Позиція № 12.2 | Запірний клапан кульового типу. |  |  |  |  |
|  | Робочий тиск |  |  | 1,0 МПа |  |
| Клапан запірний ручний кульовий, на стороні гарячої води системи ГВП | Безпечна робоча температура |  |  | 100 °C |  |
|  | Матеріал |  |  | Бронзовий або латунний корпус. Здатність роботи з паром/гарячою водою. Для Ду ≥ 50 мм дозволяється використовувати сталевий корпус з забезпеченням захисту від конденсації зовні |  |
|  | З'єднання |  |  | Фланцеве або різьбове |  |
| Позиція № 13 | Конструкція клапану повинна забезпечувати здатність роботи з брудною водою. |  |  |  |  |
| Клапан зворотний | Робочий тиск |  |  | 1,6 МПа |  |
|  | Безпечна робоча температура |  |  | 150°C |  |
|  | З'єднання |  |  | Фланцеве |  |
| Позиція № 13.1 | Робочий тиск |  |  | 1,0 МПа |  |
|  | Безпечна робоча температура |  |  | 100 °C |  |
| Клапан зворотний системи ГВП | Матеріал |  |  | Бронзовий або латунний корпус. Здатність роботи з паром/гарячою водою. |  |
|  | З'єднання |  |  | Фланцеве або різьбове |  |
|  | Теплообмінники першого та другого ступеню можуть інтегруватись в один блок на одній рамі при умові, що гідравлічна схема залишається двоступеневою. |  |  |  |  |
| Позиція № 14 Теплообмінник ГВП першого ступеню |  |  |  |  |  |
| Позиція № 15 Теплообмінник ГВП другого ступеню | Характеристики теплообмінника для підігріву води: - розбірний пластинчатий теплообмінник з ущільненням; - пластини та інші частини, що контактують з рідиною - з нержавіючої сталі марки AISI 316 або вище; - всі інші металеві частини з епоксидним або аналогічним покриттям. Встановлення теплообміннику повинно забезпечувати можливість спрощеного розбирання тільки шляхом роз’єднання фланців, без демонтажу іншого обладнання. |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа |  |
|  | Безпечна робоча температура |  |  | 150 °C |  |
| Позиція № 16 | Здвоєний циркуляційний відцентровий насос з ротором мокрого типу |  |  |  |  |
| Насос циркуляційний системи ГВП | Дозволяється використання двох циркуляційних насосів з встановленням необхідної запірно-регулюючої арматури |  |  |  |  |
|  | Насос встановлюється у відповідності до інструкцій виробника. Необхідно забезпечити можливість його обслуговування та демонтажу без розбирання трубопроводів та інших компонентів. |  |  |  |  |
|  | Тиск насосу визначається відповідно до розрахункового гідравлічного опору в системі ГВП з урахуванням гідравлічних опорів елементів модулю. Рівень шуму не більше 40 dB; |  |  |  |  |
|  | Робочий тиск |  |  | 1,0 МПа |  |
|  | Безпечна робоча температура |  |  | 80 °C |  |
|  | Живлення: ~ 220/380В, 50 Гц. |  |  |  |  |
| Позиція № 17 | Запобіжний клапан пружинного типу, з можливістю зміни тиску відкриття. |  |  |  |  |
|  | Тиск відкриття |  |  | 0,6 ÷ 1,0 МПа |  |
| Клапан запобіжний | Безпечна робоча температура |  |  | 150 °C |  |
|  | Матеріал |  |  | Здатність роботи з паром/гарячою водою. |  |
|  | З'єднання |  |  | Різьбове |  |
| Позиція № 18 | Резервуар герметичної конструкції з клапаном автоматичного випуску повітря та ручним кульовим краном з заглушкою для дренажу. |  |  |  |  |
| Повітрозбірник з клапаном повітряним випускним | Вхід в резервуар повинен бути вище, ніж вихід, на висоту не менше 5 вхідних (вихідних) діаметрів |  |  |  |  |
|  | Робочий тиск |  |  | 1,0 МПа |  |
|  | Безпечна робоча температура |  |  | 100 °C |  |
|  | З'єднання |  |  | Фланцеве |  |
| Позиція № 19 | Клапан балансувальний |  |  |  |  |
| Позиція № 20 | Грязьовик |  |  |  |  |
| Позиція № 21 | Насос дренажний |  |  |  |  |
| Позиція № 22 | Датчик рівня води в дренажному приямку |  |  |  |  |
| Позиція № 23 | Пристрій магнітної обробки води для системи гарячого водопостачання |  |  |  |  |
| Позиція № F, F1 Штуцер промивний з запірним клапаном | Штуцер промивний з запірним клапаном кульового типу з патрубком для приєднання гнучкого шлангу та з заглушкою. |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа |  |
|  | Безпечна робоча температура |  |  | 150 °C |  |
| Позиція P 1.1, Р 1.2 Манометр контактний з запірним кульовим краном | Манометр зі шкалою, що відповідає діапазону вимірювань тиску. Манометр встановлюється з кульовим запірним краном. Необхідно передбачити можливість скиду повітря та електричний сигналізатор з регульованим установочним значенням. |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа (для модуля опалення) |  |
|  |  |  |  | 1,0 МПа (для модуля ГВП) |  |
|  | Безпечна робоча температура |  |  | 150°C (для модуля опалення) |  |
|  |  |  |  | 100°C (для модуля ГВП) |  |
|  | Точність |  |  | не менше ± 2,5% від максимального значення |  |
|  | Діаметр циферблату |  |  |  100 мм |  |
|  | З'єднання |  |  | Різьбове |  |
|  | Замість електроконтактного манометра дозволяється використовувати реле тиску з можливістю ручної зміни тиску спрацювання. |  |  |  |  |
| Позиція P Манометр з краном запірним кульовим | Манометр зі шкалою, що відповідає діапазону вимірювань тиску. Манометр встановлюється з кульовим запірним краном. Передбачити можливість скиду повітря. |  |  |  |  |
|  | Робочий тиск |  |  | 1,6 МПа (для модулю опалення) |  |
|  |  |  |  | 1,0 МПа (для модулю ГВП) |  |
|  | Безпечна робоча температура |  |  | 150°C (для модулю опалення) |  |
|  |  |  |  | 100°C (для модулю ГВП) |  |
|  | Робочий тиск |  |  | 1,6 МПа (для модулю опалення) |  |
|  | Клас точності |  |  | 1,5 |  |
|  | Діаметр циферблату |  |  |  100 мм |  |
|  | З'єднання |  |  | Різьбове |  |
| Позиція T Термометр |  |  |  |  |  |
|  | Клас точності |  |  | 1 |  |
|  | Шкала |  |  | (20–150) °C для опалення |  |
|  | Шкала |  |  | (0–100) °C для хол. та гарячої води |  |
| Трубопроводи Позиції T1, T2, T11, T12 | Труби сталеві електрозварні. |  |  |  |  |
| Позиції T4, T3, B1 | Труби сталеві оцинковані |  |  |  |  |
| Ізоляція трубопроводів Позиції Т1, Т2, Т11, Т12, Т3, Т4, B1 | Виконавець повинен виконувати вимоги правил та нормативів проектування та безпеки, а також енергозбереження. Ізоляція на трубопроводах холодної води повинна захищати від конденсації. Ізоляція трубопроводів - мінераловатні фольговані циліндри, або інші волокнисті теплоізоляційні матеріали з еквівалентними технічними характеристиками, товщина визначається відповідно до таблиці Б.1 додатку Б ДНБ В 2.5-67:2013 «Опалення, вентиляція та кондиціонування» з перерахунком на фактичну теплопровідність матеріалу. |  |  |  |  |
| Теплова ізоляція теплообмінників | Виконавець повинен виконувати вимоги правил та нормативів проектування та безпеки, а також енергозбереження. Теплова ізоляція теплообмінника з волокнистих теплоізоляційних матеріалів. Ізоляція повинна легко монтуватися та зніматися. |  |  |  |  |
| Матеріали | Все обладнання та матеріали повинні бути новими, такими, що враховують всі останні покращення конструкції та матеріалів. |  |  |  |  |

| T1/ Т2 | Подавальний/ Зворотний трубопроводи тепломережі |  |
| --- | --- | --- |
| Т11/ Т12 | Подавальний / Зворотний трубопроводи системи опалення |  |
| В1 | Трубопровід холодної води |  |
| Т3 | Трубопровід гарячої води |  |
| Т4 | Циркуляційний трубопровід |  |

# 5. Опис системи дистанційного контролю та збору даних

## 5.1. Основні функції Системи:

  - цілодобовий контроль в дуплексному режимі за роботою та показниками всіх вузлів обліку водо-, тепло- та електропостачання, давачів температури з передачею даних на Сервер;

  - цілодобовий контроль за роботою складових Системи, давачів аварій, несанкціонованого доступу, внутрішньої температури будівлі;

  - можливість опитувати кожний з зазначених вузлів обліку по запиту в режимі реального часу і за розкладом, визначеним диспетчером, спостерігати отриману інформацію за допомогою персонального комп’ютера та мобільних пристроїв, підключеного до мережі Internet та роздруковувати її;

  - можливість отримувати інтегральну інформацію по кожному вузлу обліку, об’єкту, групі об’єктів, а також по Системі в цілому щодо тепло-, водо-, та електроспоживання за годину, добу, місяць, рік або за необхідний період часу.  Графічне і текстове відображення зазначених параметрів;

  - діагностика всіх складових Системи в режимі реального часу;

  - вимірювання і реєстрація температури і витрат теплоносія в прямому і зворотному трубопроводі міської тепломережі;

  - вимірювання і реєстрація температури всередині  приміщень об’єкту, що контролюється (визначається Абонентом, має знаходитися не нижче першого поверху, в приміщенні, в якому проходить основний виробничий (навчальний) процес);

  - архівування даних з можливістю відновлення інформації в разі збою Системи;

  - технологічна та аварійна сигналізація роботи насосів МІТП, затоплення теплопункту та прориву трубопроводів;

  - захист даних, що передаються Системою та сервера від несанкціонованого доступу.

## 5.2.  Програмне забезпечення.

Короткі відомості щодо програмного забезпечення (ПЗ):

Програмне забезпечення повинно бути сумісним з існуючою Системою дистанційного контролю та збору даних.

Сервер зв’язку центральної диспетчерської забезпечує отримання даних від пунктів збору та передачі даних за допомогою мережі Internet та GSM в автоматичному режимі через визначений диспетчером проміжок часу або по запиту диспетчерів, конвертацію отриманих даних  і передачу їх до сервера бази даних. В разі отримання інформації щодо аварії сервер надсилає SMS повідомлення диспетчеру обслуговуючої організації.

Сервер бази даних забезпечує зберігання і резервування отриманих даних щодо енергоспоживання.

Web-сервер забезпечує відображення даних, що знаходяться в базі даних через мережу Internet в текстовому та графічному вигляді, відповідно до прав доступу користувача.

Контролер зв’язку пункту збору і передачі інформації забезпечує збір даних від вузлів обліку та давачів і передачу їх за запитом, що надходить від серверу зв’язку центральної диспетчерської.

Програма диспетчеризації повинна забезпечити візуалізацію процесу в доступній формі з можливістю контролювання основних параметрів Системи, та з можливістю підготовки та роздрукування відомостей про роботу Системи, а також забезпечувати конвертацію даних щодо роботи Системи, стану давачів, енерго-, та водоспоживання в формати MS “Excel”).

-  Програма має формувати звіти, що включають дані щодо вибраних користувачем параметрів (серед тих, які контролюються Системою) за вибраний період (подобові, погодинні, помісячні і річні). Приклади наведені в Додатку 4-13;

- В разі, коли дані по тепло-, водо-, та електроспоживанню об’єкта надходять від декількох вузлів обліку, програма повинна відображати звіти як по окремим вузлам обліку, так і загалом по видам енергоресурсів (теплова енергія, електрична енергія, вода);

-  Інформація щодо аварійних ситуацій по всім об’єктам, включеним в Систему за вказаний період часу повинна відображатися в окремому «вікні» у вигляді: «назва об’єкту – тип аварійної ситуації – дата аварії». Має бути передбачений перехід зі згаданого «вікна» до докладних даних по об’єкту, де виявлена аварія.

Аварійні сигнали:

а) 	затоплення теплопункту (порив трубопроводів холодного та гарячого водопостачання, опалення та каналізації);

б) 	аварія насосів опалення;

в) 	аварія насосу ГВП;

г) 	не надходять дані від вузла обліку (із вказанням вузла обліку);

д) 	збій у роботі Системи чи її складових (зникло живлення і т. інш.).

СУБД – збереження архівних даних про роботу Системи. При взаємодії з програмою диспетчеризації здійснює підготовку даних для створення відомостей.

Вимоги до програмних засобів забезпечення архівування включають:

- автоматичне архівуванння;

- відновлення інформації працюючих серверів та АРМів;

- виконання процедур за запитом адміністратора або по графіку.

Допоміжні програми здійснюють вирішення специфічних задач, таких як забезпечення стійкості, захисту даних та ін.

Замовник має право самостійно перевірити достовірність наданих Учасником гарантій відповідності запропонованої до встановлення системи шляхом запиту до Виробника системи дистанційного контролю щодо тестового доступу та збору даних  системи для аналізу та підтвердження заявленого функціоналу системи.

Програми налаштування та адміністрування Системи.

Основне призначення – налаштування та адміністрування СУБД, редагування мнемосхем, зміна базових настроювань Системи.

*У разі, якщо на об’єкті встановлена система моніторингу та диспетчеризації, необхідно передбачити встановлення контролера ІТП, що буде сумісний з існуючою системою та забезпечуватиме виконання функцій згідно п. 3.7  розділу 3 - Вимоги до капітального ремонту  ІТП.

5.3 Орієнтовна схема системи дистанційного контролю:

Пристрій збору та передачі даних

теплолічильник

Система управління ІТП

Інші прилади вимірювання та контролю

Пристрій живлення

GSM модем

антена

мережа Інтернет

220VAC

сигналізація та

контроль

Рис. Схема пристрою збору даних

Перелік сигналів, що контролюються:

- Температури в приміщеннях.

- Зовнішня температура.

- Температури в подавальному та зворотному трубопроводах тепломережі (Т1, Т2).

- Температура в подавальному та зворотному трубопроводах системи опалення (Т11, Т12).

- Температура в подавальному та циркуляційному трубопроводах системи гарячого водопостачання (Т3, Т4).

- Температура холодної води.

- Витрата холодної води

- Витрата холодної води на потреби гарячого водопостачання.

- Дані з лічильників теплової енергії.

- Дані з лічильників електричної енергії.

- Інші сигнали:

  - Затоплення теплопункту;

  - Відкриття дверей;

  - Аварія насосів.

Абоненти

Сервер бази даних

(інформація про споживання, характеристики об’єкта, нештатні ситуації)

Канали зв’язку

(інтернет, локальна мережа)

Веб

сервер

-ручне введення;

-верифікація;

-звіти;

-аналіз;

Нештатні

ситуації

Веб

браузер

Веб

браузер

Енерго-менеджер

Блок аналізу і верифікації

(перевірка первинної інформації, аналіз даних тощо)

лічильник

лічильник

лічильник

Пункт збору та передачі даних

Канали зв’язку

(GSM, GPRS, інтернет, локальна мережа тощо)

лічильник

лічильник

давачі

Система управління

Система управління

Система управління

Сервер зв’язку

Рис. Схема системи дистанційного контролю

| Позиція | Опис |
| --- | --- |
| Пристрій збору та передачі даних з характеристиками | Загальні: Діапазон робочих температур: 5-55°С Вологість повітря: до 93% Клас захисту IP (не нижче): 65 Живлення: 230 В, 50 Гц, Зв’язок: GSM/3G/GPRS модем з підтримкою USSD Зовнішня GSM антена Інтерфейси зв’язку: RS-485 – 1 або більше RS-232 – 1 або більше MBUS Входи/виходи Аналоговий вхід 0-24В – 1 або більше Цифровий вхід – 1 або більше Цифровий вихід – 1 або більше Давачі температури – можливість підключення до 16 давачів температури типу 1 – wire Пристрій повинен забезпечувати: - Прийом даних від сервера зв’язку - передачу даних серверу зв’язку по протоколам обміну між сервером та контролером - перетворення протоколів передачі даних - діагностику роботи обладнання, формування і передача даних про помилки - при перебоях у зв’язку з сервером, архівування даних протягом не менше 7 діб та їх подальшу передачу при відновленні зв’язку - можливість дистанційної (по каналам GSM) конфігурації, та моніторингу роботи самого приладу |
| Лічильники імпульсів | - Автономне живлення; - Підключення по шині RS-485, RS-232, MBus - Архівація даних за період: - погодинних: не менше 30 діб; - подобових: не менше 360 діб. - Частота імпульсів, що можуть бути підраховані – не менше 16 Гц. |
| Давачі температур | - Діапазон вимірювання: -20 0С — +50 0С; - Підключення (шина 1-Wire), радіоканал |
| USB-модем | - Робота в мережах GSM (GPRS); - Можливість підключення зовнішньої антени; |

## 5.4  Монтаж системи дистанційного контролю:

Монтаж Системи повинен забезпечувати естетичний вигляд, легкість обслуговування та зручність читання показників контрольно-вимірювальних приладів.

Виконавець має забезпечити синхронізацію локальної диспетчерської (пункту збору та передачі даних на об’єкті) з центральною та передачу даних з вузлів обліку та давачів, зібраних на об’єкті до її серверів.

Зв’язок між вузлами обліку, давачами (аварійних ситуацій, внутрішньої, зовнішньої температури повітря, температури теплоносія) та контролером зв’язку може здійснюватись за допомогою дротового або радіозв’язку, з огляду на забезпечення надійності і економічності Системи.

Інформація по кожному вузлу обліку повинна оновлюватися в АРМах локальних і центральної диспетчерських автоматично через заданий адміністратором період часу (від 1 хв. до 24 годин) або позачергово за запитом адміністратора центральної чи локальних диспетчерських.

Інформація з кожного комерційного вузла обліку має містити:

- протокол (звіт) за добу – погодинний;

- протокол (звіт) за місяць – подобовий;

- протокол позаштатних ситуацій.

Інформація з давачів аварійної сигналізації  та внутрішньої температури будівлі:

- протокол аварійних ситуацій;

- протокол даних щодо внутрішньої температури повітря – погодинний (максимальна, середня і мінімальна температури).

Давачі внутрішньої температури приміщення можуть бути під’єднані до контролеру зв’язку.

Система повинна виконувати архівацію даних 1 раз на добу в нічний час.

Програмне забезпечення повинне бути захищене від несанкціонованого доступу. Аварійні сигнали повинні передаватися першочергово - безпосередньо після виникнення такої ситуації: «контролер зв’язку  – сервер зв’язку – диспетчер обслуговуючої організації».

Всі виконані роботи та надані матеріали повинні відповідати нормативам проектування та стандартам безпеки, що діють на території України.

Зв’язок між вузлами обліку, давачами (аварійних ситуацій, внутрішньої, зовнішньої температури повітря, температури теплоносія) та контролером зв’язку може здійснюватись за допомогою дротового або радіозв’язку, з огляду на забезпечення надійності і економічності Системи.

Програмне забезпечення має контролювати параметри в запитах користувача. Невірний набір параметрів не повинен сприйматися Системою та шкодити її функціонуванню.

Живлення складових Системи має відбуватися від загальної електричної мережі напругою 200-230 В з частотою 50 Гц.

Складові системі повинні мати енергонезалежну пам’ять для забезпечення збереження інформації в разі відсутності живлення.

# 6. Інші вимоги

Все обладнання, що встановлюється, повинне мати технічні паспорти. Усі матеріали, частини, обладнання і компоненти збірної конструкції в цілому і ті, що постачаються окремо, повинні супроводжуватися паспортами, стандартними і спеціальними інструкціями з установки й експлуатації, як це вимагає існуюча виробнича практика.

Інструкції з експлуатації та інша технічна документація повинні бути українською  мовою.

## 6.1. Вимоги по технічному обслуговуванню і ремонту.

Обладнання, що встановлюється повинне вимагати тільки звичайного технічного обслуговування і сезонних оглядів. Вимоги у відношенні технічного обслуговування, такого як чищення, промивання, регулювання і змащення обладнання і т.д., повинні бути заздалегідь визначені в технічному паспорті та в інструкціях по експлуатації комплектуючого обладнання.

6.2. Вимоги до навчання відповідального персоналу.

Для забезпечення навчання персоналу, відповідального за обслуговування обладнання індивідуальних теплових пунктів та осіб, задіяних в роботі системи дистанційного контролю та збору даних, Виконавець має надати обслуговуючому персоналу відповідні інструкції та провести навчання цього персоналу, або надати доступ до відеокурсу навчання (можливе проведення вебінару), з обслуговування та користування встановленим обладнанням, системою дистанційного контролю, тощо.

ДОДАТОК ДО ТЕХНІЧНОГО ЗАВДАННЯ НА ВИКОНАННЯ БУДІВЕЛЬНИХ РОБІТ З КАПІТАЛЬНОГО РЕМОНТУ  ІНДИВІДУАЛЬНИХ ТЕПЛОВИХ ПУНКТІВ  В ГРОМАДСЬКИХ БУДІВЛЯХ М. КИЄВА

ПРИКЛАД ПРОТОКОЛІВ, ЩО ФОРМУЮТЬСЯ СИСТЕМОЮ

| Міністерство (відомство) | Договір №__ від |
| --- | --- |
| Належність до бюджету | Код Споживача |
| Належність до типу бюджету | Адреса |
| Галузева належність |  |
| Адміністративний район |  |
| Код території |  |
| Код ЄДРПОУ |  |
| Форма власності |  |
| Форма фінансування |  |

ПРОТОКОЛ
погодинне споживання електроенергії

із 10.05.2007 по 10.05.2007

Лічильник. Модель_________ Серійний номер ____________

| Дата Час |  | Споживання, квт. год |  |
| --- | --- | --- | --- |
| 10.05.2007 00:00:00 |  | 0,000 |  |
| 10.05.2007 01:00:00 |  | 0,000 |  |
| 10.05.2007 02:00:00 |  | 0,000 |  |
| 10.05.2007 03:00:00 |  | 0,000 |  |
| 10.05.2007 04:00:00 |  | 0,000 |  |
| 10.05.2007 05:00:00 |  | 0,000 |  |
| 10.05.2007 06:00:00 |  | 0,000 |  |
| 10.05.2007 07:00:00 |  | 1,850 |  |
| 10.05.2007 08:00:00 |  | 8,000 |  |
| 10.05.2007 09:00:00 |  | 9,750 |  |
| 10.05.2007 10:00:00 |  | 8,400 |  |
| 10.05.2007 11:00:00 |  | 10,450 |  |
| 10.05.2007 12:00:00 |  | 7,900 |  |
| 10.05.2007 13:00:00 |  | 7,050 |  |
| 10.05.2007 14:00:00 |  | 5,550 |  |
| 10.05.2007 15:00:00 |  | 3,250 |  |
| 10.05.2007 16:00:00 |  | 2,250 |  |
| 10.05.2007 17:00:00 |  | 1,650 |  |
| 10.05.2007 18:00:00 |  | 1,400 |  |
| Показники лічильника: |  |  |  |
| за попередній період, квт.год — 4885,950 |  |  |  |
| за поточний період, квт.год — 4957,600 |  |  |  |
| Сумарне споживання за поточний період, квт.год — 71,650 |  |  |  |
| Міністерство (відомство) |  |  |  | Договір №___ від___ |  |  |
| Належність до бюджету |  |  |  | Код Споживача |  |  |
| Належність до типу бюджету |  |  |  | Адреса |  |  |
| Галузева належність |  |  |  |  |  |  |
| Адміністративний район |  |  |  |  |  |  |
| Код території |  |  |  |  |  |  |
| Код ЄДРПОУ |  |  |  |  |  |  |
| Форма власності |  |  |  |  |  |  |
| Форма фінансування |  |  |  |  |  |  |

ПРОТОКОЛ

добове споживання електроенергії

із 10.04.2007 по 10.05.2007

Лічильник                Модель___________Серійний номер___________

Назва Адреса:

|  | 10.04 | 11.04 | 12.04 | 13.04 | 14.04 | 15.04 | 16.04 | 17.04 | 18.04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Споживання, кВт. год | 15,35 | 46,75 | 52,90 | 48,85 | 22,15 | 0,05 | 51,85 | 60,90 | 41,15 |
|  | 19.04 | 20.04 | 21.04 | 23.04 | 24.04 | 25.04 | 26.04 | 27.04 | 28.04 |
| Споживання, кВт. год | 105,55 | 77,25 | 2,55 | 57,40 | 62,00 | 47,10 | 61,35 | 42,55 | 9,65 |
|  | 29.04 | 30.04 | 01.05 | 02.05 | 03.05 | 04.05 | 05.05 | 06.05 | 07.05 |
| Споживання, кВт. год | 0,00 | 0,00 | 0,00 | 0,05 | 96,15 | 59,70 | 48,80 | 4,45 | 64,40 |
|  | 08.05 | 09.05 | 10.05 |  |  |  |  |  |  |
| Споживання, кВт. год | 54,40 | 0,05 | 71,65 |  |  |  |  |  |  |

Показники лічильника:

за попередній період, кВт.год — 3752,600

за поточний період, кВт.год — 4957,600

Сумарне споживання за поточний період, квт.год — 1205,000

| "СПОЖИВАЧ" |  |
| --- | --- |
| Керівник підприємства |  |
| Відповідальна за теплопункт особа | М.П. |

| Міністерство (відомство) | Договір №___ від |
| --- | --- |
| Належність до бюджету | Код Споживача |
| Належність до типу бюджету | Адреса |
| Галузева належність |  |
| Адміністративний район |  |
| Код території |  |
| Код ЄДРПОУ |  |
| Форма власності |  |
| Форма фінансування |  |

ПРОТОКОЛ

добового споживання води

із 10.04.2007 по 10.05.2007

Назва Адреса:

Лічильник вода ХВП. Модель          Серійний номер

| Дата |  | Споживання, м3 |  |
| --- | --- | --- | --- |
| 10.04.2007 |  | 7,00 |  |
| 11.04.2007 |  | 13,80 |  |
| 12.04.2007 |  | 11,80 |  |
| 13.04.2007 |  | 18,00 |  |
| 14.04.2007 |  | 6,90 |  |
| 15.04.2007 |  | 3,70 |  |
| 16.04.2007 |  | 17,40 |  |
| 17.04.2007 |  | 16,20 |  |
| 18.04.2007 |  | 15,60 |  |
| 19.04.2007 |  | 15,10 |  |
| 20.04.2007 |  | 19,00 |  |
| 21.04.2007 |  | 0,90 |  |
| 23.04.2007 |  | 27,80 |  |
| 24.04.2007 |  | 14,70 |  |
| 25.04.2007 |  | 12,90 |  |
| 26.04.2007 |  | 12,90 |  |
| 27.04.2007 |  | 15,20 |  |
| 28.04.2007 |  | 7,30 |  |
| 29.04.2007 |  | 5,30 |  |
| 30.04.2007 |  | 4,70 |  |
| 01.05.2007 |  | 4,90 |  |
| 02.05.2007 |  | 4,50 |  |
| 03.05.2007 |  | 15,50 |  |
| 04.05.2007 |  | 14,20 |  |
| 05.05.2007 |  | 12,20 |  |
| Показники лічильника: |  |
| за попередній період, м3 — 1569,300 |  |
| за поточний період, м3 — 1917,800 |  |
| Сумарне споживання за поточний період, м3 — 348,500 |  |

| "СПОЖИВАЧ" |  |  |  |
| --- | --- | --- | --- |
| Керівник підприємства |  |  |  |
| Відповідальна за теплопункт особа |  |  | М.П. |
| Міністерство (відомство) | Договір №__ від |  |  |
| Належність до бюджету | Код Споживача |  |  |
| Належність до типу бюджету | Адреса |  |  |
| Галузева належність |  |  |  |
| Адміністративний район |  |  |  |
| Код території |  |  |  |
| Код ЄДРПОУ |  |  |  |
| Форма власності |  |  |  |
| Форма фінансування |  |  |  |

ПРОТОКОЛ
погодинного споживання води

із 10.05.2007 по 10.05.2007

Лічильник вода ХВП. Модель              Серійний номер

Назва Адреса:

| Дата Час |  |  | Споживання, м3 |  |  |
| --- | --- | --- | --- | --- | --- |
| 10.05.2007 00:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 01:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 02:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 03:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 04:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 05:00:00 |  |  | 0,400 |  |  |
| 10.05.2007 06:00:00 |  |  | 0,600 |  |  |
| 10.05.2007 07:00:00 |  |  | 0,500 |  |  |
| 10.05.2007 08:00:00 |  |  | 0,600 |  |  |
| 10.05.2007 09:00:00 |  |  | 0,900 |  |  |
| 10.05.2007 10:00:00 |  |  | 1,300 |  |  |
| 10.05.2007 11:00:00 |  |  | 1,600 |  |  |
| 10.05.2007 12:00:00 |  |  | 1,700 |  |  |
| 10.05.2007 13:00:00 |  |  | 1,700 |  |  |
| 10.05.2007 14:00:00 |  |  | 1,100 |  |  |
| 10.05.2007 15:00:00 |  |  | 0,500 |  |  |
| 10.05.2007 16:00:00 |  |  | 0,400 |  |  |
| 10.05.2007 17:00:00 |  |  | 0,300 |  |  |
| 10.05.2007 18:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 19:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 20:00:00 |  |  | 0,200 |  |  |
| 10.05.2007 21:00:00 |  |  | 0,300 |  |  |
| 10.05.2007 22:00:00 |  |  | 0,100 |  |  |
| 10.05.2007 23:00:00 |  |  | 0,200 |  |  |
| Показники лічильника: |  |  |
| за попередній період, м3 — 1904,000 |  |  |
| за поточний період, м3 — 1917,800 |  |  |
| Сумарне споживання за поточний період, м3 — 13,800 |  |  |

ПРОТОКОЛ
реєстрації добових параметрів та підсумкових значень теплоспоживання
із 10.04.2007 по 10.05.2007

Назва Адреса:

| Особовий рахунок |  |  |  |  |  | Лічильник тепла |  |  |  |  |  |  |  |  |  | Ду = |  |  |  |  |  | N |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Договірні навантаження |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Загальна |  |  |  |  |  |  |  |  | Гкал/год |  |  |  |  |  | Запрограмовані значення |  |  |  |  |  |  |  |  |  |  |  |
| Опалювання |  |  |  |  |  |  |  |  | Гкал/год |  |  |  |  |  | T3 = C |  |  |  |  |  |  | dTmin = C |  |  |  |  |
| ГВС |  |  |  |  |  |  |  |  | Гкал/год |  |  |  |  |  | Q1max = m3/год |  |  |  |  |  |  | Q1min = % |  |  |  |  |
| Вентиляція |  |  |  |  |  |  |  |  | Гкал/год |  |  |  |  |  | Q2max = m3/год |  |  |  |  |  |  | Q2min = % |  |  |  |  |
| Дата |  | T1 °C |  |  | T2 °C |  |  |  | T3 °C |  |  | E МВтч |  |  | E Гкал |  |  | G1 T |  | G2 T |  |  |  | (G1-G2) T |
| 10.04.2007 |  | 61,09 |  |  | 42,52 |  |  |  |  |  |  | 3,97 |  |  | 3,41 |  |  | 183,69 |  | 187,34 |  |  |  | -3,65 |
| 11.04.2007 |  | 60,80 |  |  | 42,15 |  |  |  |  |  |  | 4,08 |  |  | 3,51 |  |  | 186,78 |  | 190,70 |  |  |  | -3,92 |
| 12.04.2007 |  | 60,96 |  |  | 42,32 |  |  |  |  |  |  | 3,93 |  |  | 3,38 |  |  | 180,87 |  | 184,74 |  |  |  | -3,87 |
| 13.04.2007 |  | 55,98 |  |  | 37,94 |  |  |  |  |  |  | 2,31 |  |  | 1,99 |  |  | 121,27 |  | 124,07 |  |  |  | -2,80 |
| 14.04.2007 |  | 42,89 |  |  | 30,69 |  |  |  |  |  |  | 0,01 |  |  | 0,01 |  |  | 5,70 |  | 6,45 |  |  |  | -0,75 |
| 15.04.2007 |  | 24,93 |  |  | 18,53 |  |  |  |  |  |  | 0,00 |  |  | 0,00 |  |  | 0,96 |  | 1,44 |  |  |  | -0,48 |
| 16.04.2007 |  | 36,06 |  |  | 21,54 |  |  |  |  |  |  | 0,03 |  |  | 0,03 |  |  | 5,48 |  | 6,22 |  |  |  | -0,74 |
| 17.04.2007 |  | 46,27 |  |  | 30,01 |  |  |  |  |  |  | 0,19 |  |  | 0,16 |  |  | 11,39 |  | 12,42 |  |  |  | -1,03 |
| 18.04.2007 |  | 44,95 |  |  | 30,12 |  |  |  |  |  |  | 0,25 |  |  | 0,21 |  |  | 12,59 |  | 13,61 |  |  |  | -1,02 |
| 19.04.2007 |  | 41,11 |  |  | 26,89 |  |  |  |  |  |  | 0,23 |  |  | 0,20 |  |  | 11,18 |  | 12,19 |  |  |  | -1,01 |
| 20.04.2007 |  | 41,24 |  |  | 27,75 |  |  |  |  |  |  | 0,23 |  |  | 0,20 |  |  | 11,18 |  | 11,95 |  |  |  | -0,77 |
| 21.04.2007 |  | 33,71 |  |  | 25,55 |  |  |  |  |  |  | 0,03 |  |  | 0,03 |  |  | 5,96 |  | 6,69 |  |  |  | -0,73 |
| 22.04.2007 |  | 25,93 |  |  | 18,85 |  |  |  |  |  |  | 0,00 |  |  | 0,00 |  |  | 2,39 |  | 3,11 |  |  |  | -0,72 |
| 23.04.2007 |  | 40,17 |  |  | 26,89 |  |  |  |  |  |  | 0,23 |  |  | 0,20 |  |  | 11,42 |  | 12,43 |  |  |  | -1,01 |
| 24.04.2007 |  | 40,72 |  |  | 27,80 |  |  |  |  |  |  | 0,18 |  |  | 0,15 |  |  | 9,28 |  | 10,27 |  |  |  | -0,99 |
| 25.04.2007 |  | 40,36 |  |  | 28,00 |  |  |  |  |  |  | 0,19 |  |  | 0,16 |  |  | 9,99 |  | 10,99 |  |  |  | -1,00 |
| 26.04.2007 |  | 40,41 |  |  | 28,17 |  |  |  |  |  |  | 0,16 |  |  | 0,14 |  |  | 9,28 |  | 10,27 |  |  |  | -0,99 |
| 27.04.2007 |  | 42,03 |  |  | 26,42 |  |  |  |  |  |  | 0,25 |  |  | 0,21 |  |  | 11,65 |  | 12,67 |  |  |  | -1,02 |
| 28.04.2007 |  | 35,42 |  |  | 27,37 |  |  |  |  |  |  | 0,01 |  |  | 0,01 |  |  | 4,77 |  | 5,50 |  |  |  | -0,73 |
| 29.04.2007 |  | 24,32 |  |  | 18,31 |  |  |  |  |  |  | 0,00 |  |  | 0,00 |  |  | 1,43 |  | 2,16 |  |  |  | -0,73 |
| 30.04.2007 |  | 36,88 |  |  | 29,00 |  |  |  |  |  |  | 0,04 |  |  | 0,03 |  |  | 5,96 |  | 6,93 |  |  |  | -0,97 |
| 01.05.2007 |  | 38,59 |  |  | 29,86 |  |  |  |  |  |  | 0,03 |  |  | 0,03 |  |  | 6,19 |  | 7,16 |  |  |  | -0,97 |
| 02.05.2007 |  | 38,33 |  |  | 29,45 |  |  |  |  |  |  | 0,03 |  |  | 0,03 |  |  | 5,71 |  | 6,69 |  |  |  | -0,98 |
| 03.05.2007 |  | 40,21 |  |  | 28,00 |  |  |  |  |  |  | 0,17 |  |  | 0,15 |  |  | 10,23 |  | 11,23 |  |  |  | -1,00 |
| 04.05.2007 |  | 42,08 |  |  | 29,27 |  |  |  |  |  |  | 0,20 |  |  | 0,17 |  |  | 9,99 |  | 10,99 |  |  |  | -1,00 |
| 05.05.2007 |  | 35,28 |  |  | 23,92 |  |  |  |  |  |  | 0,16 |  |  | 0,14 |  |  | 8,10 |  | 9,09 |  |  |  | -0,99 |
| 06.05.2007 |  | 24,45 |  |  | 17,73 |  |  |  |  |  |  | 0,00 |  |  | 0,00 |  |  | 1,67 |  | 2,40 |  |  |  | -0,73 |
| 07.05.2007 |  | 39,51 |  |  | 26,05 |  |  |  |  |  |  | 0,22 |  |  | 0,19 |  |  | 10,71 |  | 11,71 |  |  |  | -1,00 |
| 08.05.2007 |  | 40,82 |  |  | 27,59 |  |  |  |  |  |  | 0,20 |  |  | 0,17 |  |  | 9,99 |  | 10,99 |  |  |  | -1,00 |
| 09.05.2007 |  | 39,09 |  |  | 29,01 |  |  |  |  |  |  | 0,05 |  |  | 0,04 |  |  | 6,43 |  | 7,40 |  |  |  | -0,97 |
| 10.05.2007 |  | 39,93 |  |  | 27,77 |  |  |  |  |  |  | 0,19 |  |  | 0,16 |  |  | 10,23 |  | 11,23 |  |  |  | -1,00 |
|  |  | Сер. знач. |  |  | Сер. знач. |  |  |  | Сер. знач. |  |  | Сума |  |  | Сума |  |  | Сума |  | Сума |  |  |  | Сума |
|  |  | 40,47 |  |  | 28,24 |  |  |  | 0,00 |  |  | 17,57 |  |  | 15,11 |  |  | 882,47 |  | 921,04 |  |  |  | -38,57 -4,37% від G1 |
| E попередній період |  |  | 10,00 Гкал |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| E поточний період |  |  | 25,11 Гкал |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

ПРОТОКОЛ
реєстрації погодинних параметрів та підсумкових значень теплоспоживання
із 10.05.2007 по 10.05.2007

Назва Адреса:

| Особовий рахунок |  |  | Лічильник тепла |  |  | Ду = |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Договірні навантаження |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Загальна |  |  |  |  | Гкал/год |  |  |  | Запрограмовані значення |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Опалювання |  |  |  |  | Гкал/год |  |  |  | T3 = C |  |  |  |  | dTmin = C |  |  |  |  |  |  |  |  |  |
| ГВС |  |  |  |  | Гкал/год |  |  |  | Q1max = m3/год |  |  |  |  | Q1min = % |  |  |  |  |  |  |  |  |  |
| Вентиляція |  |  |  |  | Гкал/год |  |  |  | Q2max = m3/год |  |  |  |  |  | Q2min = % |  |  |  |  |  |  |  |  |
| Дата |  | Час | Q1 m3/год |  | Q2 m3/год |  |  | T1 °C |  |  | T2 °C |  | T3 °C |  |  |  | G1 T |  | G2 T |  |  |
| 10.05.2007 |  | 00:00:00 | 0,03 |  | 0,06 |  |  | 27,87 |  |  | 19,40 |  |  |  |  |  | 0,03 |  | 0,06 |  |  |
| 10.05.2007 |  | 01:00:00 | 0,03 |  | 0,06 |  |  | 26,37 |  |  | 19,03 |  |  |  |  |  | 0,03 |  | 0,06 |  |  |
| 10.05.2007 |  | 02:00:00 | 0,03 |  | 0,06 |  |  | 25,11 |  |  | 18,74 |  |  |  |  |  | 0,03 |  | 0,06 |  |  |
| 10.05.2007 |  | 03:00:00 | 0,03 |  | 0,06 |  |  | 24,08 |  |  | 18,47 |  |  |  |  |  | 0,03 |  | 0,06 |  |  |
| 10.05.2007 |  | 04:00:00 | 0,03 |  | 0,06 |  |  | 23,27 |  |  | 18,19 |  |  |  |  |  | 0,03 |  | 0,06 |  |  |
| 10.05.2007 |  | 05:00:00 | 0,03 |  | 0,06 |  |  | 22,63 |  |  | 17,97 |  |  |  |  |  | 0,03 |  | 0,06 |  |  |
| 10.05.2007 |  | 06:00:00 | 0,10 |  | 0,14 |  |  | 22,11 |  |  | 17,80 |  |  |  |  |  | 0,10 |  | 0,14 |  |  |
| 10.05.2007 |  | 07:00:00 | 1,58 |  | 1,64 |  |  | 42,31 |  |  | 28,83 |  |  |  |  |  | 1,57 |  | 1,63 |  |  |
| 10.05.2007 |  | 08:00:00 | 0,55 |  | 0,60 |  |  | 52,52 |  |  | 34,80 |  |  |  |  |  | 0,54 |  | 0,60 |  |  |
| 10.05.2007 |  | 09:00:00 | 0,68 |  | 0,73 |  |  | 50,27 |  |  | 42,20 |  |  |  |  |  | 0,67 |  | 0,72 |  |  |
| 10.05.2007 |  | 10:00:00 | 0,81 |  | 0,86 |  |  | 51,14 |  |  | 39,50 |  |  |  |  |  | 0,80 |  | 0,85 |  |  |
| 10.05.2007 |  | 11:00:00 | 0,70 |  | 0,75 |  |  | 52,44 |  |  | 36,22 |  |  |  |  |  | 0,69 |  | 0,74 |  |  |
| 10.05.2007 |  | 12:00:00 | 1,63 |  | 1,68 |  |  | 54,11 |  |  | 30,65 |  |  |  |  |  | 1,61 |  | 1,67 |  |  |
| 10.05.2007 |  | 13:00:00 | 0,96 |  | 1,01 |  |  | 55,12 |  |  | 30,10 |  |  |  |  |  | 0,95 |  | 1,00 |  |  |
| 10.05.2007 |  | 14:00:00 | 1,17 |  | 1,22 |  |  | 54,21 |  |  | 33,28 |  |  |  |  |  | 1,15 |  | 1,21 |  |  |
| 10.05.2007 |  | 15:00:00 | 1,37 |  | 1,42 |  |  | 55,55 |  |  | 28,67 |  |  |  |  |  | 1,35 |  | 1,41 |  |  |
| 10.05.2007 |  | 16:00:00 | 0,51 |  | 0,56 |  |  | 52,93 |  |  | 40,29 |  |  |  |  |  | 0,50 |  | 0,56 |  |  |
| 10.05.2007 |  | 17:00:00 | 0,02 |  | 0,05 |  |  | 48,00 |  |  | 40,58 |  |  |  |  |  | 0,02 |  | 0,05 |  |  |
| 10.05.2007 |  | 18:00:00 | 0,02 |  | 0,05 |  |  | 42,94 |  |  | 35,42 |  |  |  |  |  | 0,02 |  | 0,05 |  |  |
| 10.05.2007 |  | 19:00:00 | 0,02 |  | 0,06 |  |  | 39,66 |  |  | 28,80 |  |  |  |  |  | 0,02 |  | 0,06 |  |  |
| 10.05.2007 |  | 20:00:00 | 0,02 |  | 0,06 |  |  | 37,20 |  |  | 24,58 |  |  |  |  |  | 0,02 |  | 0,06 |  |  |
| 10.05.2007 |  | 21:00:00 | 0,02 |  | 0,06 |  |  | 34,96 |  |  | 22,16 |  |  |  |  |  | 0,02 |  | 0,06 |  |  |
| 10.05.2007 |  | 22:00:00 | 0,02 |  | 0,06 |  |  | 32,79 |  |  | 20,78 |  |  |  |  |  | 0,02 |  | 0,06 |  |  |
| 10.05.2007 |  | 23:00:00 | 0,02 |  | 0,06 |  |  | 30,63 |  |  | 19,98 |  |  |  |  |  | 0,02 |  | 0,06 |  |  |
|  |  |  | Сер. знач. |  | Сер. знач. |  |  | Сер. знач. |  |  | Сер. знач. |  | Сер. знач. |  |  |  |  | Сума |  |  | Сума |  |
|  |  |  | 0,43 |  | 0,47 |  |  | 39,93 |  |  | 27,77 |  | 0,00 |  |  |  |  | 10,25 |  |  | 11,29 |  |
| "СПОЖИВАЧ" |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Керівник підприємства |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Відповідальна за теплопункт особа |  |  |  |  |  |  |  |  |  |  |  |  |  | М.П. |  |  |  |  |  |

ПРОТОКОЛ
реєстрації температури всередині приміщення (подобовий)
із 10.04.2007 по 10.05.2007

Назва Адреса:

| Дата | T сер °C | T макс °C | T мін °C |
| --- | --- | --- | --- |
| 10.04.2007 | 21 | 25 | 18 |
| 11.04.2007 | 21 | 25 | 18 |
| 12.04.2007 | 21 | 25 | 18 |
| 13.04.2007 | 21 | 25 | 18 |
| 14.04.2007 | 21 | 25 | 18 |
| 15.04.2007 | 21 | 25 | 18 |
| 16.04.2007 | 21 | 25 | 18 |
| 17.04.2007 | 21 | 25 | 18 |
| 18.04.2007 | 21 | 25 | 18 |
| 19.04.2007 | 21 | 25 | 18 |
| 20.04.2007 | 21 | 25 | 18 |
| 21.04.2007 | 21 | 25 | 18 |
| 22.04.2007 | 21 | 25 | 18 |
| 23.04.2007 | 21 | 25 | 18 |
| 24.04.2007 | 21 | 25 | 18 |
| 25.04.2007 | 21 | 25 | 18 |
| 26.04.2007 | 21 | 25 | 18 |
| 27.04.2007 | 21 | 25 | 18 |
| 28.04.2007 | 21 | 25 | 18 |
| 29.04.2007 | 21 | 25 | 18 |
| 30.04.2007 | 21 | 25 | 18 |
| 01.05.2007 | 21 | 25 | 18 |
| 02.05.2007 | 21 | 25 | 18 |
| 03.05.2007 | 21 | 25 | 18 |
| 04.05.2007 | 21 | 25 | 18 |
| 05.05.2007 | 21 | 25 | 18 |
| 06.05.2007 | 21 | 25 | 18 |
| 07.05.2007 | 21 | 25 | 18 |
| 08.05.2007 | 21 | 25 | 18 |
| 09.05.2007 | 21 | 25 | 18 |
| 10.05.2007 | 21 | 25 | 18 |
|  | Сер. знач. | Макс. знач. | Сер. знач. |
|  | 21 | 25 | 18 |

| "СПОЖИВАЧ" |  |
| --- | --- |
| Керівник підприємства |  |
| Відповідальна за теплопункт особа | М.П. |

ПРОТОКОЛ
реєстрації температури всередині приміщення (погодинний)
із 10.04.2007 по 10.05.2007

Назва Адреса:

| Дата | T сер °C | T макс °C | T мін °C |
| --- | --- | --- | --- |
| 10.05.2007 00:00:00 | 21 | 25 | 18 |
| 10.05.2007 01:00:00 | 21 | 25 | 18 |
| 10.05.2007 02:00:00 | 21 | 25 | 18 |
| 10.05.2007 03:00:00 | 21 | 25 | 18 |
| 10.05.2007 04:00:00 | 21 | 25 | 18 |
| 10.05.2007 05:00:00 | 21 | 25 | 18 |
| 10.05.2007 06:00:00 | 21 | 25 | 18 |
| 10.05.2007 07:00:00 | 21 | 25 | 18 |
| 10.05.2007 08:00:00 | 21 | 25 | 18 |
| 10.05.2007 09:00:00 | 21 | 25 | 18 |
| 10.05.2007 10:00:00 | 21 | 25 | 18 |
| 10.05.2007 11:00:00 | 21 | 25 | 18 |
| 10.05.2007 12:00:00 | 21 | 25 | 18 |
| 10.05.2007 13:00:00 | 21 | 25 | 18 |
| 10.05.2007 14:00:00 | 21 | 25 | 18 |
| 10.05.2007 15:00:00 | 21 | 25 | 18 |
| 10.05.2007 16:00:00 | 21 | 25 | 18 |
| 10.05.2007 17:00:00 | 21 | 25 | 18 |
| 10.05.2007 18:00:00 | 21 | 25 | 18 |
| 10.05.2007 19:00:00 | 21 | 25 | 18 |
| 10.05.2007 20:00:00 | 21 | 25 | 18 |
| 10.05.2007 21:00:00 | 21 | 25 | 18 |
| 10.05.2007 22:00:00 | 21 | 25 | 18 |
| 10.05.2007 23:00:00 | 21 | 25 | 18 |
|  | Сер. знач. | Макс. знач. | Сер. знач. |
|  | 21 | 25 | 18 |

| "СПОЖИВАЧ" |  |
| --- | --- |
| Керівник підприємства |  |
| Відповідальна за теплопункт особа | М.П. |

ПРОТОКОЛ
реєстрації аварійних сигналів
із 10.04.2007 по 10.05.2007

Назва Адреса:

| Дата | № сигналу | Назва сигналу |
| --- | --- | --- |
| 25.04.2007 06:15:46 | 0 | Нормальний стан |
| 25.04.2007 12:04:13 | 0 | Нормальний стан |
| 25.04.2007 13:39:06 | 0 | Нормальний стан |
| 25.04.2007 17:46:00 | 0 | Нормальний стан |
| 25.04.2007 18:55:07 | 0 | Нормальний стан |
| 26.04.2007 07:58:41 | 0 | Нормальний стан |
| 26.04.2007 11:20:27 | 0 | Нормальний стан |
|  | 17 | Доступ в приміщення |
|  | 18 | Поруш електропостачання |
|  | 19 | Аварiйне електроживлення |
|  | 17 | Доступ в приміщення |
|  | 18 | Поруш електропостачання |
|  | 19 | Аварiйне електроживлення |
| 26.04.2007 14:06:36 | 9 | Прорив трубопровода |
|  | 17 | Доступ в приміщення |
|  | 18 | Порушення електропостачання |

IІ. Технічне завдання

на виконання будівельних робіт з капітального ремонту систем опалення в громадських будівлях м. Києва

Метою виконання робіт з капітального ремонту систем опалення є підвищення ефективності її роботи, поліпшення комфорту всередині приміщень, подовження терміну експлуатації інженерних систем будівлі.

Існуюча ситуація

Джерелом теплопостачання є індивідуальні теплові пункти, розташовані у підвальних приміщеннях або в окремих будівлях. Підключення систем опалення здійснюється від розподільчих гребінок в ІТП. Система опалення з вертикальними стояками та нижнім розведенням. Як теплоносій для систем опалення й теплопостачання прийнята гаряча вода з параметрами 95-70°С. Контур системи опалення обладнаний автоматикою з можливістю зниження температури у неробочий час (нічний, вихідні та святкові дні). Існуючі системи опалення експлуатується тривалий час і, в більшості випадків, жодного разу не промивались (гідравлічним або хімічним методом). Регулювання роботою опалювальних приладів в окремих приміщень не передбачено.

Проектні рішення

Проєктною документацією передбачається заміна існуючих опалювальних приладів. Опалювальні прилади встановлюються вільно під віконним простором, в місцях доступних для ремонту, огляду та очищення. Довжина опалювальних приладів визначена розрахунком та прийнята не менше ніж 75% довжини світлового прорізу (вікна), згідно з п.6.7.5 ДБН В.2.5-67:2013. Передбачено встановлення декоративних екранів на опалювальні прилади, що виключають можливість травмування та отримання опіків, з обов’язковим кріпленням до стіни, відповідно до чинних будівельних норм, нормативних документів, стандартів.

Передбачається заміна магістралей системи опалення, а також демонтаж існуючої обв’язки опалювальних приладів та обв’язка трубами нових. Існуюча схема системи опалення змінюється на двотрубну вертикальну із встановленням необхідної запірної та балансувальної арматури. Компенсація теплових подовжень трубопроводів здійснюється за рахунок кутів поворотів.

На кожному опалювальному приладі передбачено встановлення автоматичного термостатичного клапану типу з термостатичним елементом. На зворотному трубопроводі  до опалювальних приладів встановлюється запірний пристрій.

Опалювальні прилади у сходових клітинах розміщуються на висоті 2,2 м від поверхні сходових площадок до низу радіаторів, згідно п. 5.42 ДБН В.1.1-7-2002.

В місцях підключення стояків системи опалення до магістралей системи опалення, передбачається установка пари автоматичних балансувальних клапанів. Також, встановлюється муфтовий кульовий кран на зворотному трубопроводі перед клапаном для можливості відсічення потоку без зміни попереднього налагодження.

Видалення повітря із систем опалення й теплопостачання здійснюється через автоматичні повітровипускні клапани, встановлених у верхніх точках системи в ІТП. Опалювальні прилади обладнані кранами Маєвського.

Для спорожнювання трубопроводів у нижніх частинах систем передбачається установка дренажних кранів з патрубком для приєднання шлангу в ІТП.

Системи опалення повинні бути виконані зі сталевих водогазопровідних труб відповідно до вимог чинних нормативно-технічних документів.

Передбачено виконання трубопроводів систем опалення й теплопостачання зі сталевих водогазопровідних труб відповідно до вимог чинних будівельних норм, нормативних документів, стандартів для зовнішніх діаметрів до 60 включно та зі сталевих електрозварювальних труб відповідно до вимог чинних будівельних норм, нормативних документів, стандартів для зовнішніх діаметрів вище 60.

Трубопроводи системи опалення з опалювальними приладами прокладаються окремо від трубопроводів теплопостачання водопідігрівачів (якщо передбачається).

Для стояків системи опалення по можливості використовувати існуючі отвори в перекритті розширив їх до необхідного діаметру. Після проведення демонтажу існуючих опалювальних приладів виконати відновлення покриття стін. Передбачити заробляння отворів у місцях проходу труб через перекриття.

Система опалення та її складові, що демонтуються передаються балансоутримувачу згідно акту.

З метою зниження втрат тепла магістралей системи опалення, що розташовані в підвалі покриваються тепловою ізоляцією фольгованою в циліндрах. Товщина теплової ізоляції прийнята згідно з табл. Б1, ДБН В.2.5-67:2013. Розводки труб в середині приміщень вкриваються ізоляцією на основі спіненого поліетилену.

Внутрішня температура в приміщеннях:

| Тип приміщення | Нормована температура, °C |
| --- | --- |
| Ігрові приміщення, роздягальні, медкабінет, туалетні кімнати в зимовий період | +22 |
| Спальні в зимовий період | +21 |
| Зона рекреації, коридор | +18 |
| Кабінети в зимовий період | +18 |
| Гардероб та підсобні приміщення | +18 |
| Кухня | +16 |
| Спортивні та музичні зали | +19 |
| Приміщення басейну | +30 |
| Пральня | +18 |
| Кабінет фізіотерапії, масажу | +28 |
| Венткамера | +16 |
| Сходові клітини (для всіх поверхів) | +18 |

В приміщеннях ігрових кімнат 1-го поверху передбачається підігрів підлоги - система "тепла підлога" (для дошкільних навчальних закладів). Приєднання контурів "теплої підлоги" до системи опалення відбувається після вузла змішування. Вузол змішування встановлюється в ІТП та складається з термостатичного клапану з накладним датчиком температури та циркуляційного насоса. В приміщеннях з "теплою підлогою" встановлюються розподільчі колектори в шафах прихованого монтажу. На розподільчій гребінці передбачається встановлення витратомірів. Температура підлоги в ігрових кімнатах прийнята 23 °C. Підтримання постійної температури підлоги відбувається завдяки зонному клапану з сервоприводом, що управляється від термостату програматора з датчиком температури підлоги. Як теплоносій для системи "тепла підлога" прийнята гаряча вода з параметрами 30-25°С (остаточну температуру на подачі прийняти в процесі пуско-налагоджування відповідно до заданої температури підлоги).

Загальний орієнтовний перелік будівельних робіт, який можливий при проведенні капітального ремонту систем опалення в громадських будівлях м. Києва наведений нижче:

- Демонтаж трубопроводів внутрішньої системи опалення (де передбачено проектом);

- Прокладання трубопроводів внутрішньої системи опалення (де передбачено проектом);

- Демонтаж/монтаж опалювальних приладів (де передбачено проектом);

- Відновлення покриття стін після демонтажу старого обладнання;

- Підключення опалювальних приладів до трубопроводів внутрішньої системи опалення (де передбачено проектом);

- Встановлення запірної та регулюючої арматури (де передбачено проектом);

- Балансування системи опалення шляхом встановлення балансувальних клапанів;

- Проведення пусконалагоджувальних робіт та введення обладнання в експлуатацію;

- Прибирання місць проведення робіт та вивезення сміття;

- Навчання персоналу

Детальний перелік об’єму робіт на матеріалів для кожного об’єкту наданий в Розділі IІІ. Форми Тендерних пропозицій -  Форма Прейскуранту. За погодженням із Замовником при виконанні контракту зазначений перелік може бути доповнений та/або змінений.

Всі посилання в прейскуранті на конкретну торговельну марку чи фірму, джерело походження матеріалів або виробника, вважати індикативною інформацією. Учасник може запропонувати матеріали і обладнання інших виробників, які мають такі ж, або кращі, характеристики.

## Загальні технічні вимоги

1. Учасник повинен надати документи, що підтверджують відповідність Учасника  технічним  вимогам виконання робіт:

Копія діючої протягом повного періоду виконання робіт ліцензії на право здійснення відповідного виду діяльності (господарська діяльність, пов’язана із створенням об’єктів архітектури/господарська діяльність з будівництва об’єктів) та копію додатку до неї (перелік робіт провадження господарської діяльності), де обов’язково наявна інформація про категорію складності не нижче ІIІ та/або клас наслідків (відповідальності) об’єктів будівництва – не нижче класу СС2 - незначні наслідки з обов’язковою наявністю таких робіт:

- монтаж технологічного устаткування;

- виконання пусконалагоджувальних робіт (визначається ліцензіатом за видами технологічного устаткування);

- монтаж внутрішніх інженерних мереж, систем, приладів і засобів вимірювання, водопроводу та каналізації, опалення, технологічних трубопроводів, технологічних систем, електропостачання, електрообладнання і електроосвітлення, автоматизації і контрольно-вимірювальних приладів.

У разі залучення субпідрядника – надати  копію діючої протягом повного періоду виконання робіт ліцензії субпідрядника та копію додатку до неї, (перелік робіт провадження господарської діяльності, які буде виконувати субпідрядник та які підлягають ліцензуванню).

Виконавець несе повну відповідальність щодо дотримання норм та правил з охорони праці та техніки безпеки під час виконання робіт та отримання всіх необхідних дозволів, ліцензій, декларацій (в тому числі на виконання зварювальних робіт), сертифікатів, повідомлень, тощо.

2. Виконавець повинен підібрати основне та додаткове обладнання і матеріали відповідно до проектної документації. Проектна документація надається Замовником учаснику тендеру за вимогою, що складається у довільній формі.

3. Технологічні компоненти систем опалення повинні бути серійного виробництва, мати якість, що відповідає вимогам міжнародних стандартів, бути атестованими в Державному Комітеті України із стандартизації згідно з законодавством України. Все енергоспоживаюче обладнання повинне бути атестоване як високоефективне.

4. Всі виконані роботи та надані матеріали повинні відповідати українським та міжнародним правилам і нормативам проектування та стандартам безпеки, ДБН В.2.5-39:2008 «Теплові мережі» тощо.

Роботи повинні виконуватись з дотриманням ДСТУ (ГОСТ), ДБН, Правил користування тепловою енергією, Правил електро- та пожежної безпеки, Охорони праці та інших нормативних документів, що діють на території України, зокрема:

- ДБН А.2.2-3-2014 «Склад та зміст проектної документації на будівництво»;

- ДБН В.2.5-56:2014 «Системи протипожежного захисту»;

- ДБН В.2.2-3:2018 «Заклади освіти. Будинки і споруди»;

- ДБН В.2.2-4:2018 «Заклади дошкільної освіти. Будинки і споруди»;

- ДБН В.2.5-67:2013 - «Опалення, вентиляція та кондиціонування»;

- ДСТУ-НБ В.1.1-27:2010 «Будівельна кліматологія»;

- ДСТУ-Н Б В.2.5-73:2013 «Настанова з монтажу внутрішніх санітарно
технічних систем»;

- ДБН В.1.1-7:2016 "Пожежна безпека об’єктів будівництва. Загальні вимоги";

- ДБН В.2.6-31:2021 "Теплова ізоляція та енергоефективність будівель".

Заходи, передбачені проєктною документацією, повинні забезпечити безпечну експлуатацію системи.

# 5. Інші вимоги

Все обладнання, що встановлюється, повинне мати технічні паспорти. Усі матеріали, частини, обладнання і компоненти збірної конструкції в цілому і ті, що постачаються окремо, повинні супроводжуватися паспортами, стандартними і спеціальними інструкціями з установки й експлуатації, як це вимагає існуюча виробнича практика.

## 5.1. Вимоги по технічному обслуговуванню і ремонту.

Обладнання, що встановлюється повинне вимагати тільки звичайного технічного обслуговування і сезонних оглядів. Вимоги у відношенні технічного обслуговування, такого як чищення, промивання, регулювання і змащення обладнання і т.д., повинні бути заздалегідь визначені в технічному паспорті та в інструкціях по експлуатації комплектуючого обладнання.

5.2. Вимоги до навчання відповідального персоналу.

Для забезпечення навчання персоналу, відповідального за обслуговування обладнання системи опалення, Виконавець має надати обслуговуючому персоналу відповідні інструкції та провести навчання цього персоналу, або надати доступ до відеокурсу навчання (можливе проведення вебінару), з обслуговування та користування встановленим обладнанням.

5.3.  Гарантійні зобов'язання

Якість виконаних робіт повинна гарантуватися за Договором щонайменше впродовж  2  років з Дати завершення (відповідно до Розділу А пункту 1.1. (g) ЗУК).

Термін гарантії на обладнання, що встановлене при проведенні капітального ремонту системи опалення – згідно гарантії виробника обладнання, зазначеної у Паспорті (гарантійному талоні) обладнання.

Виконавець також зобов’язується:

(а) власними силами передати балансоутримувачу об’єкта все демонтоване обладнання та матеріали за Актами прийому-передачі та повідомити про це Замовника протягом 5 (п’яти) робочих днів з моменту їх демонтажу.

(б) звільнити Об'єкт від техніки, невикористаних матеріалів, будівельного сміття після закінчення виконання Робіт протягом 7 (семи) календарних днів з моменту завершення Робіт;

(г) Нести відповідальність за збереження матеріальних цінностей на Об’єкті, освітлення й огородження його, дотримання санітарних і протипожежних вимог, складування будівельних матеріалів і техніки, охорону праці й техніку безпеки при проведенні робіт в умовах щільної житлової забудови та інших правил, що застосовуються при здійсненні ремонтно-будівельних робіт;

(д) забезпечувати замовлення, постачання, приймання, розвантаження, складування, зберігання, подавання на будівельний майданчик матеріалів, конструкцій та обладнання, контроль якості, кількості та комплектності постачання цих ресурсів

5.4. Екологічні вимоги

5.4.1 Демонтовані матеріали та обладнання, що не підлягають повторному використанню, а також будівельні відходи та сміття повинні вивозитись і утилізовуватись у відповідності до вимог українського законодавства.

5.4.2 Не допускається використання матеріалів, що містять азбест.

5.4.3 Азбестові відходи розглядаються в Україні як небезпечні відходи. Наказ міністерства охорони здоров'я №762 від 10.01.2012 «Про затвердження Державних санітарних норм і правил Про безпеку і захист працівників від шкідливого впливу азбесту і азбестовмісних матеріалів», містить конкретні положення по роботах та обробці таких матеріалів.

Це означає, що проведення ремонтних робіт можливе тільки після демонтажу азбесту, особливо азбестоцементного брухту та азбестової крихти які розглядаються як промислові небезпечні відходи IV класу які в подальшому піддають конкретному кваліфікованому поводженню. Це означає, що при виявленні необхідності демонтажу виробів з азбестових матеріалів, підрядник зобов'язаний залучити спеціалізовану компанію або мати ліцензію на роботи з матеріалами, що містять азбест: збір, зберігання, транспортування, очищення, прибирання та захоронення відповідно до Закону України "Про забезпечення санітарного та епідемічного добробуту населення" Стаття 13 Ліцензування господарської діяльності, пов'язаної з потенційною небезпекою для здоров'я людини. Види господарської діяльності, пов'язані з потенційною небезпекою для здоров'я людини, підлягають ліцензуванню у випадках, встановлених законом. Ліцензійні умови щодо видів господарської діяльності, які пов'язані з потенційною небезпекою для здоров'я людини, обов'язково включають вимоги щодо забезпечення санітарного та епідеміологічного благополуччя населення.

IІІ. Графік поставки обладнання, матеріалів і завершення робіт з капітального ремонту  індивідуальних теплових пунктів та систем опалення у громадських будівлях м. Києва

Необхідна дата поставки обладнання та матеріалів на об'єкт - не пізніше 30 квітня 2024р.

Необхідна дата завершення робіт - не пізніше 01 листопада 2024р.

| Види робіт | Тривалість реалізації |
| --- | --- |
| Поставка обладнання та матеріалів | 4-8 тижнів з дати підписання контракту |
| Виконання монтажно-демонтажних робіт, введення в експлуатацію | 6-8 місяців з дати підписання контракту |

1. Графік виконання робіт розробляється підрядником  по видах робіт на основі проектно - кошторисної документації та нормативних термінів виконання будівельно – монтажних робіт.

2. Графік виконання робіт є невід’ємною частиною контрактної угоди.

Section V.  General Conditions of Contract

These General Conditions of Contract (GCC), read in conjunction with the Particular Conditions (PCC) and other documents listed therein, constitute a complete document expressing the rights and obligations of the parties. These General Conditions of Contract have been developed on the basis of considerable international experience in the drafting and management of contracts, bearing in mind a trend in the construction industry towards simpler, more straightforward language. The GCC can be used for both smaller contracts and lump sum contracts.

A. General

| Definitions | - Boldface type is used to identify defined terms. - The Accepted Contract Amount means the amount accepted in the Letter of Acceptance for the execution and completion of the Works and the remedying of any defects. - The Activity Schedule is a schedule of the activities comprising the construction, installation, testing, and commissioning of the Works in a lump sum contract. It includes a lump sum price for each activity, which is used for valuations and for assessing the effects of Variations and Compensation Events. - The Adjudicator is the person appointed jointly by the Employer and the Contractor to resolve disputes in the first instance, as provided for in GCC 23. - NEFCO means the financing institution named in the PCC. - Bill of Quantities means the priced and completed Price Schedules forming part of the Tender. - Compensation Events are those defined in GCC Clause 42 hereunder. - The Completion Date is the date of completion of the Works as certified by the Project Manager, in accordance with GCC Sub-Clause 53.1. - The Contract is the Contract between the Employer and the Contractor to execute, complete, and technical maintenance. It consists of the documents listed in GCC Sub-Clause 2.3 below. - The Contractor is the party whose Tender to carry out the Works has been accepted by the Employer. - The Contractor’s Tender is the completed tender document submitted by the Contractor to the Employer. - The Contract Price is the Accepted Contract Amount stated in the Letter of Acceptance and thereafter as adjusted in accordance with the Contract. - Days are calendar days; months are calendar months. - Dayworks are varied work inputs subject to payment on a time basis for the Contractor’s employees and Equipment, in addition to payments for associated Materials and Plants. - A Defect is any part of the Works not completed in accordance with the Contract. - The Defects Liability Certificate is the certificate issued by Project Manager upon correction of defects by the Contractor. - The Defects Liability Period is the period named in the PCC pursuant to Sub-Clause 34.1 and calculated from the Completion Date. - Drawings means the drawings of the Works, as included in the Contract, and any additional and modified drawings issued by (or on behalf of) the Employer in accordance with the Contract, include calculations and other information provided or approved by the Project Manager for the execution of the Contract. - The Employer is the party who employs the Contractor to carry out the Works, as specified in the PCC. - Equipment is the Contractor’s machinery and vehicles brought temporarily to the Site to construct the Works. - “In writing” or “written” means hand-written, type-written, printed or electronically made, and resulting in a permanent record; - The Initial Contract Price is the Contract Price listed in the Employer’s Letter of Acceptance. - The Intended Completion Date is the date on which it is intended that the Contractor shall complete the Works. The Intended Completion Date is specified in the PCC. The Intended Completion Date may be revised only by the Project Manager by issuing an extension of time or an acceleration order. - Materials are all supplies, including consumables, used by the Contractor for incorporation in the Works. - Plant is any integral part of the Works that shall have a mechanical, electrical, chemical, or biological function. - The Project Manager is the person named in the PCC (or any other competent person appointed by the Employer and notified to the Contractor, to act in replacement of the Project Manager) who is responsible for supervising the execution of the Works and administering the Contract. - PCC means Particular Conditions of Contract. - The Site is the area defined as such in the PCC. - Site Investigation Reports are those that were included in the tender documents and are factual and interpretative reports about the surface and subsurface conditions at the Site. - Specification means the Specification of the Works included in the Contract and any modification or addition made or approved by the Project Manager. - The Start Date is given in the PCC. It is the latest date when the Contractor shall commence execution of the Works. It does not necessarily coincide with any of the Site Possession Dates. - A Subcontractor is a person or corporate body who has a Contract with the Contractor to carry out a part of the work in the Contract, which includes work on the Site. - Temporary Works are works designed, constructed, installed, and removed by the Contractor that are needed for construction or installation of the Works. - A Variation is an instruction given by the Project Manager which varies the Works. - The Works are what the Contract requires the Contractor to construct, install, and turn over to the Employer, as defined in the PCC. - Payment certificate is work performance report issued by Contractor according to form Kb2v and Statement of the value of the work performed according to form Kb3. |
| --- | --- |
| Interpretation | - In interpreting these GCC, words indicating one gender include all genders. Words indicating the singular also include the plural and words indicating the plural also include the singular. Headings have no significance. Words have their normal meaning under the language of the Contract unless specifically defined. The Project Manager shall provide instructions clarifying queries about these GCC. - If sectional completion is specified in the PCC, references in the GCC to the Works, the Completion Date, and the Intended Completion Date apply to any Section of the Works (other than references to the Completion Date and Intended Completion Date for the whole of the Works). - The documents forming the Contract shall be interpreted in the following order of priority: - Agreement, - Letter of Acceptance, - Contractor’s Tender, - Particular Conditions of Contract, - General Conditions of Contract, - Specifications, - Drawings, - Bill of Quantities, and - any other document listed in the PCC as forming part of the Contract. |
| Language and Law | - The language of the Contract and the law governing the Contract are stated in the PCC. - Throughout the execution of the Contract, the Contractor shall comply with the import of goods and services prohibitions in the Employer’s country, when (a) as a matter of law or official regulations, the Borrowers country prohibits commercial relations with that country; or (b) by an act of compliance with a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations, the Borrower’s Country prohibits any import of goods from that country or any payments to any person, or entity in that country. |
| Project Manager’s Decisions | - Except where otherwise specifically stated, the Project Manager shall decide contractual matters between the Employer and the Contractor in the role representing the Employer. |
| Delegation | - Unless otherwise specified in the PCC, the Project Manager may delegate any of his duties and responsibilities to other people, except to the Adjudicator, after notifying the Contractor, and may revoke any delegation after notifying the Contractor. |
| Communications | - Communications between parties that are referred to in the Conditions shall be effective only when in writing. A notice shall be effective only when it is delivered. |
| Subcontracting | - The Contractor may subcontract with the approval of the Project Manager, but may not assign the Contract without the approval of the Employer in writing. Subcontracting shall not alter the Contractor’s obligations. |
| Other Contractors | - The Contractor shall cooperate and share the Site with other contractors, public authorities, utilities, and the Employer between the dates given in the Schedule of Other Contractors, as referred to in the PCC. The Contractor shall also provide facilities and services for them as described in the Schedule. The Employer may modify the Schedule of Other Contractors, and shall notify the Contractor of any such modification. |
| Personnel and Equipment | - The Contractor shall employ the key personnel and use the equipment identified in its Tender, to carry out the Works, or other personnel and equipment approved by the Project Manager. The Project Manager shall approve any proposed replacement of key personnel and equipment only if their relevant qualifications or characteristics are substantially equal to or better than those proposed in the Tender. - If the Project Manager asks the Contractor to remove a person who is a member of the Contractor’s staff or work force, stating the reasons, the Contractor shall ensure that the person leaves the Site within seven days and has no further connection with the work in the Contract. - If the Employer, Project Manager or Contractor determines, that any employee of the Contractor be determined to have engaged in corrupt, fraudulent, coercive, collusive or Obstructive Practice during the execution of the Works, then that employee shall be removed in accordance with Clause 9.2 above. |
| Employer’s and Contractor’s Risks | - The Employer carries the risks which this Contract states are Employer’s risks, and the Contractor carries the risks which this Contract states are Contractor’s risks. |
| Employer’s Risks | - From the Start Date until the Defects Liability Certificate has been issued, the following are the Employer’s risks: - The risk of personal injury, death, or loss of or damage to property (excluding the Works, Plant, Materials, and Equipment), which are due to - negligence, breach of statutory duty, or interference with any legal right by the Employer or by any person employed by or contracted to him except the Contractor. - The risk of damage to the Works, Plant, Materials, and Equipment to the extent that it is due to a fault of the Employer or in the Employer’s design, or due to war or radioactive contamination directly affecting the country where the Works are to be executed. - From the Completion Date until the Defects Liability Certificate has been issued, the risk of loss of or damage to the Works, Plant, and Materials is an Employer’s risk except loss or damage due to - a Defect which existed on the Completion Date, - an event occurring before the Completion Date, which was not itself an Employer’s risk, or - the activities of the Contractor on the Site after the Completion Date. |
| Contractor’s Risks | 12.1 From the Starting Date until the Defects Liability Certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the Works, Plant, Materials, and Equipment) which are not Employer’s risks are Contractor’s risks. |
| Insurance | - The Contractor shall provide, in the joint names of the Employer and the Contractor, insurance cover from the Start Date to the end of the Defects Liability Period, in the amounts and deductibles stated in the PCC for the following events which are due to the Contractor’s risks: - loss of or damage to the Works, Plant, and Materials; - loss of or damage to Equipment; - loss of or damage to property (except the Works, Plant, Materials, and Equipment) in connection with the Contract; and - personal injury or death. - Policies and certificates for insurance shall be delivered by the Contractor to the Project Manager for the Project Manager’s approval before the Start Date. All such insurance shall provide for compensation to be payable in the types and proportions of currencies required to rectify the loss or damage incurred. - If the Contractor does not provide any of the policies and certificates required, the Employer may effect the insurance contract which the Contractor should have provided and recover the premiums the Employer has paid from payments otherwise due to the Contractor or, if no payment is due, the payment of the premiums shall be a debt due. - Alterations to the terms of an insurance shall not be made without the approval of the Project Manager. - Both parties shall comply with any conditions of the insurance policies. |
| Site Data | - The Contractor shall be deemed to have examined any Site Data referred to in the PCC, supplemented by any information available to the Contractor. |
| Contractor to Construct the Works | - The Contractor shall construct and install the Works in accordance with the Specifications and Drawings. |
| The Works to Be Completed by the Intended Completion Date | - The Contractor may commence execution of the Works on the Start Date and shall carry out the Works in accordance with the Program/Works schedule submitted by the Contractor, as updated with the approval of the Project Manager, and complete them by the Intended Completion Date. |
| Approval by the Project Manager | - The Contractor shall submit Specifications and Drawings showing the proposed Temporary Works to the Project Manager, for his approval. - The Contractor shall be responsible for design of Temporary Works. - The Project Manager’s approval shall not alter the Contractor’s responsibility for design of the Temporary Works. - The Contractor shall obtain approval of third parties to the design of the Temporary Works, where required. - All Drawings prepared by the Contractor for the execution of all types of Works, are subject to prior approval by the Project Manager before this use. |
| Safety | - The Contractor shall be responsible for the safety of all activities on the Site. |
| Discoveries | - Anything of historical or other interest or of significant value unexpectedly discovered on the Site shall be the property of the Employer. The Contractor shall notify the Project Manager of such discoveries and carry out the Project Manager’s instructions for dealing with them. |
| Possession of the Site | - The Employer shall give access Site to the Contractor. If right to access to Site or its part required for Works execution is not given by the date stated in the PCC, the Employer shall be deemed to have delayed the start of the relevant activities, and this shall be a Compensation Event. |
| Access to the Site | - The Contractor shall allow the Project Manager and any person authorized by the Project Manager access to the Site and to any place where work in connection with the Contract is being carried out or is intended to be carried out. |
| Instructions, Inspections and Audits | - The Contractor shall carry out all instructions of the Project Manager which comply with the applicable laws where the Site is located. - The Contractor shall keep, and shall make all reasonable efforts to cause its Subcontractors and subconsultants to keep, accurate and systematic accounts and records in respect of the Works in such form and details as will clearly identify relevant time changes and costs. - The Contractor shall permit and shall cause its Subcontractors and subconsultants to permit, NEFCO and/or persons appointed by NEFCO to inspect the Site and/or the accounts and records relating to the performance of the Contract and the submission of the Tender, and to have such accounts and records audited by auditors appointed by NEFCO if requested by NEFCO. The Contractor’s and its Subcontractors’ and subconsultants’ attention is drawn to Sub-Clause 25.1 which provides, inter alia, that acts intended to materially impede the exercise of NEFCO’s inspection and audit rights provided for under Sub-Clause 22.2 constitute a Prohibited Practice subject to contract termination (as well as to a determination of ineligibility pursuant to NEFCO’s prevailing sanctions procedures). |
| Appointment of the Adjudicator | - The Adjudicator shall be appointed jointly by the Employer and the Contractor, at the time of the Employer’s issuance of the Letter of Acceptance. If, in the Letter of Acceptance, the Employer does not agree on the appointment of the Adjudicator, the Employer will request the Appointing Authority designated in the PCC, to appoint the Adjudicator within 14 days of receipt of such request. - Should the Adjudicator resign or die, or should the Employer and the Contractor agree that the Adjudicator is not functioning in accordance with the provisions of the Contract, a new Adjudicator shall be jointly appointed by the Employer and the Contractor. In case of disagreement between the Employer and the Contractor, within 30 days, the Adjudicator shall be designated by the Appointing Authority designated in the PCC at the request of either party, within 14 days of receipt of such request. |
| Procedure for Disputes | - If the Contractor believes that a decision taken by the Project Manager was either outside the authority given to the Project Manager by the Contract or that the decision was wrongly taken, the decision shall be referred to the Adjudicator within 14 days of the notification of the Project Manager’s decision. - The Adjudicator shall give a decision in writing within 28 days of receipt of a notification of a dispute. - The Adjudicator shall be paid by the hour at the rate specified in the PCC, together with reimbursable expenses of the types specified in the PCC, and the cost shall be divided equally between the Employer and the Contractor, whatever decision is reached by the Adjudicator. Either party may refer a decision of the Adjudicator to an Arbitrator within 28 days of the Adjudicator’s written decision. If neither party refers the dispute to arbitration within the above 28 days, the Adjudicator’s decision shall be final and binding. - The arbitration shall be conducted in accordance with the arbitration procedures published by the institution named and in the place specified in the PCC. |
| Corrupt and fraudulent practices | - NEFCO requires compliance with its policy in regard to Prohibited Practices as set forth in Clause 56 of the GCC. - The Employer requires the Contractor to disclose any commissions or fees that may have been paid or are to be paid to agents or any other party with respect to the tendering process or execution of the Contract. The information disclosed must include at least the name and address of the agent or other party, the amount and currency, and the purpose of the commission, gratuity or fee. |

B. Time Control of Works execution

| Program/Works schedule | - Within the time stated in the PCC, after the date of the Letter of Acceptance, the Contractor shall submit to the Project Manager for approval a Program/Works schedule showing the general methods, arrangements, order, and timing for all the activities in the Works. In the case of a lump sum contract, the activities in the Program/Works schedule shall be consistent with those in the Activity Schedule. - An update of the Program/Works schedule shall be a program showing the actual progress achieved on each activity and the effect of the progress achieved on the timing of the remaining work, including any changes to the sequence of the activities. - The Contractor shall submit to the Project Manager for approval an updated Program/Works schedule at intervals no longer than the period stated in the PCC. If the Contractor does not submit an updated Program/Works schedule within this period, the Project Manager may withhold the amount stated in the PCC from the next payment certificate and continue to withhold this amount until the next payment after the date on which the overdue Program/Works schedule has been submitted. In the case of a lump sum contract, the Contractor shall provide an updated Activity Schedule within 14 days of being instructed to by the Project Manager. - The Project Manager’s approval of the Program/Works schedule shall not alter the Contractor’s obligations. The Contractor may revise the Program/Works schedule and submit it to the Project Manager again at any time. A revised Program/Works schedule shall show the effect of Variations and Compensation Events. |
| --- | --- |
| Extension of the Intended Completion Date | - The Project Manager shall extend the Intended Completion Date if a Compensation Event occurs or a Variation is issued which makes it impossible for Completion to be achieved by the Intended Completion Date without the Contractor taking steps to accelerate the remaining work, which would cause the Contractor to incur additional cost. - The Project Manager shall decide whether and by how much to extend the Intended Completion Date within 21 days of the Contractor asking the Project Manager for a decision upon the effect of a Compensation Event or Variation and submitting full supporting information. If the Contractor has failed to give early warning of a delay or has failed to cooperate in dealing with a delay, the delay by this failure shall not be considered in assessing the new Intended Completion Date. |
| Acceleration | - When the Employer wants the Contractor to finish before the Intended Completion Date, the Project Manager shall obtain priced proposals for achieving the necessary acceleration from the Contractor. If the Employer accepts these proposals, the Intended Completion Date shall be adjusted accordingly and confirmed by both the Employer and the Contractor. - If the Contractor’s priced proposals for an acceleration are accepted by the Employer, they are incorporated in the Contract Price and treated as a Variation. |
| Delays Ordered by the Project Manager | - The Project Manager may instruct the Contractor to delay the start or progress of any activity within the Works. |
| Management Meetings | - Either the Project Manager or the Contractor may require the other to attend a management meeting. The business of a management meeting shall be to review the plans for remaining work and to deal with matters raised in accordance with the early warning procedure. - The Project Manager shall record the business of management meetings and provide copies of the record to those attending the meeting and to the Employer. The responsibility of the parties for actions to be taken shall be decided by the Project Manager either at the management meeting or after the management meeting and stated in writing to all who attended the meeting. |
| Early Warning | - The Contractor shall warn the Project Manager at the earliest opportunity of specific likely future events or circumstances that may adversely affect the quality of the work, increase the Contract Price, or delay the execution of the Works. The Project Manager may require the Contractor to provide an estimate of the expected effect of the future event or circumstance on the Contract Price and Completion Date. The estimate shall be provided by the Contractor as soon as reasonably possible. - The Contractor shall cooperate with the Project Manager in making and considering proposals for how the effect of such an event or circumstance can be avoided or reduced by anyone involved in the work and in carrying out any resulting instruction of the Project Manager. |

C. Quality Control

| Identifying Defects | - The Project Manager shall check the Contractor’s work and notify the Contractor of any Defects that are found. Such checking shall not affect the Contractor’s responsibilities. The Project Manager may instruct the Contractor to search for a Defect and to uncover and test any work that the Project Manager considers may have a Defect. |
| --- | --- |
| Tests | - If the Project Manager instructs the Contractor to carry out a test not specified in the Specification to check whether any work has a Defect and the test shows that it does, the Contractor shall pay for the test and any samples. If there is no Defect, the test shall be a Compensation Event. |
| Correction of Defects | - The Project Manager shall give notice to the Contractor of any Defects before the end of the Defects Liability Period, which begins at Completion, and is defined in the PCC. The Defects Liability Period shall be extended for as long as Defects remain to be corrected. - Every time notice of a Defect is given, the Contractor shall correct the notified Defect within the length of time specified by the Project Manager’s notice. |
| Uncorrected Defects | - If the Contractor has not corrected a Defect within the time specified in the Project Manager’s notice, the Project Manager shall assess the cost of having the Defect corrected, and the Contractor shall pay this amount. |

D. Cost Control

| Contract Price | - Price schedule shall contain priced items for the Works to be performed by the Contractor. Price schedule is used to calculate the Contract Price. The Contractor will be paid for the quantity of the work accomplished at the rate in the Price schedule for each item. |
| --- | --- |
| Changes in the Contract Price | - If the final quantity of the work done differs from the quantity in the Price schedule for the particular item by more than 25 percent, provided the change exceeds 1 percent of the Initial Contract Price, the Project Manager shall adjust the rate to allow for the change. The Project Manager shall not adjust rates from changes in quantities if thereby the Initial Contract Price is exceeded by more than 15 percent, except with the prior approval of the Employer. - If requested by the Project Manager, the Contractor shall provide the Project Manager with a detailed cost breakdown of any rate in the Price schedule. |
| Variations | - All Variations shall be included in updated Program/Works schedules produced by the Contractor. - The Contractor shall provide the Project Manager with a quotation for carrying out the Variation when requested to do so by the Project Manager. The Project Manager shall assess the quotation, which shall be given within seven (7) days of the request or within any longer period stated by the Project Manager and before the Variation is ordered. - If the Contractor’s quotation is unreasonable, the Project Manager may order the Variation and make a change to the Contract Price, which shall be based on the Project Manager’s own forecast of the effects of the Variation on the Contractor’s costs. - If the Project Manager decides that the urgency of varying the work would prevent a quotation being given and considered without delaying the work, no quotation shall be given and the Variation shall be treated as a Compensation Event. - The Contractor shall not be entitled to additional payment for costs that could have been avoided by giving early warning. - If the work in the Variation corresponds to an item description in the Price schedule and if, in the opinion of the Project Manager, the quantity of work above the limit stated in Sub-Clause 28.1 or the timing of its execution do not cause the cost per unit of quantity to change, the rate in the Price schedule shall be used to calculate the value of the Variation. If the cost per unit of quantity changes, or if the nature or timing of the work in the Variation does not correspond with items in the Price schedule, the quotation by the Contractor shall be in the form of new rates for the relevant items of work. |
| Cash Flow Forecasts | - When the Program/Works schedule is updated, the Contractor shall provide the Project Manager with an updated cash flow forecast. The cash flow forecast shall include different currencies, as defined in the Contract, converted as necessary using the Contract exchange rates. |
| Payment Certificates | - The Contractor shall submit to the Project Manager monthly statements of the estimated value of the work executed less the cumulative amount certified previously. - The Project Manager shall check the Contractor’s monthly statement and certify the amount to be paid to the Contractor. - The value of work executed shall be determined by the Project Manager. - The value of work executed shall comprise the value of the quantities of work in the Price schedule that have been completed. - The value of work executed shall include the valuation of Variations and Compensation Events. - The Project Manager may exclude any item certified in a previous certificate or reduce the proportion of any item previously certified in any certificate in the light of later information. |
| Payments | - Payments shall be adjusted for deductions for advance payments and retention. The Employer shall pay the Contractor the amounts certified by the Project Manager within 28 days of the date of each certificate. If the Employer makes a late payment, the Contractor shall be paid interest on the late payment in the next payment. Interest shall be calculated from the date by which the payment should have been made up to the date when the late payment is made at the prevailing rate of interest for commercial borrowing for each of the currencies in which payments are made. - If an amount certified is increased in a later certificate or as a result of an award by the Adjudicator or an Arbitrator, the Contractor shall be paid interest upon the delayed payment as set out in this clause. Interest shall be calculated from the date upon which the increased amount would have been certified in the absence of dispute. - Unless otherwise stated, all payments and deductions shall be paid or charged in the proportions of currencies comprising the Contract Price. - Items of the Works for which no rate or price has been entered in shall not be paid for by the Employer and shall be deemed covered by other rates and prices in the Contract. |
| - Compensation Events | - The following shall be Compensation Events: - The Employer does not give access to a part of the Site by the Site Possession Date pursuant to GCC Sub-Clause 20.1. - The Employer modifies the Schedule of Other Contractors in a way that affects the work of the Contractor under the Contract. - The Project Manager orders a delay or does not issue Drawings, Specifications, or instructions required for execution of the Works on time. - The Project Manager instructs the Contractor to uncover or to carry out additional tests upon work, which is then found to have no Defects. - The Project Manager unreasonably does not approve a subcontract to be let. - Ground conditions are substantially more adverse than could reasonably have been assumed before issuance of the Letter of Acceptance from the information issued to tenderers (including the Site Investigation Reports), from information available publicly and from a visual inspection of the Site. - The Project Manager gives an instruction for dealing with an unforeseen condition, caused by the Employer, or additional work required for safety or other reasons. - Other contractors, public authorities, utilities, or the Employer does not work within the dates and other constraints stated in the Contract, and they cause delay or extra cost to the Contractor. - The advance payment is delayed. - The effects on the Contractor of any of the Employer’s Risks. - The Project Manager unreasonably delays issuing a Certificate of Completion. - If a Compensation Event would cause additional cost or would prevent the work being completed before the Intended Completion Date, the Contract Price shall be increased and/or the Intended Completion Date shall be extended. The Project Manager shall decide whether and by how much the Contract Price shall be increased and whether and by how much the Intended Completion Date shall be extended. - As soon as information demonstrating the effect of each Compensation Event upon the Contractor’s forecast cost has been provided by the Contractor, it shall be assessed by the Project Manager, and the Contract Price shall be adjusted accordingly. If the Contractor’s forecast is deemed unreasonable, the Project Manager shall adjust the Contract Price based on the Project Manager’s own forecast. The Project Manager shall assume that the Contractor shall react competently and promptly to the event. - The Contractor shall not be entitled to compensation to the extent that the Employer’s interests are adversely affected by the Contractor’s not having given early warning or not having cooperated with the Project Manager. |
| Tax | - The Project Manager shall adjust the Contract Price if taxes, duties, and other levies are changed between the date 28 days before the submission of Tenders for the Contract and the date of the last Completion certificate. The adjustment shall be the change in the amount of tax payable by the Contractor, provided such changes are not already reflected in the Contract Price or are a result of GCC Clause 44. |
| Currencies | - Where payments are made in currencies other than the currency of the Employer’s country specified in the PCC, the exchange rates used for calculating the amounts to be paid shall be the exchange rates stated in the Contractor’s Tender. |
| Retention | - The Employer shall retain from each payment due to the Contractor the proportion stated in the PCC until Completion of the whole of the Works. - Upon the issue of a Certificate of Completion of the Works by the Project Manager, in accordance with GCC 51.1, half the total amount retained shall be repaid to the Contractor and half when the Defects Liability Period has passed and the Project Manager has certified that all Defects notified by the Project Manager to the Contractor before the end of this period have been corrected. The Contractor may substitute retention money with an “on demand” Bank Guarantee. |
| Liquidated Damages | - The Contractor shall pay liquidated damages to the Employer at the rate per day stated in the PCC for each day that the Completion Date is later than the Intended Completion Date. The total amount of liquidated damages shall not exceed the amount defined in the PCC. The Employer may deduct liquidated damages from payments due to the Contractor. Payment of liquidated damages shall not affect the Contractor’s liabilities. - If the Intended Completion Date is extended after liquidated damages have been paid, the Project Manager shall correct any overpayment of liquidated damages by the Contractor by adjusting the next payment certificate. The Contractor shall be paid interest on the overpayment, calculated from the date of payment to the date of repayment, at the rates specified in GCC Sub-Clause 41.1. |
| Advance Payment | - The Employer shall make advance payment to the Contractor of the amounts stated in the PCC by the date stated in the PCC. - The Contractor is to use the advance payment only to pay for Equipment, Plant, Materials, and mobilization expenses required specifically for execution of the Contract. The Contractor shall demonstrate that advance payment has been used in this way by supplying copies of invoices or other documents to the Project Manager. - The advance payment shall be repaid by deducting proportionate amounts from payments otherwise due to the Contractor, following the schedule of completed percentages of the Works on a payment basis. No account shall be taken of the advance payment or its repayment in assessing valuations of work done, Variations, price adjustments, Compensation Events, Bonuses, or Liquidated Damages. |
| Securities | - The Performance Security shall be provided to the Employer no later than the date specified in the Letter of Acceptance and shall be issued in an amount specified in the PCC, by a bank or surety acceptable to the Employer, and denominated in the types and proportions of the currencies in which the Contract Price is payable. The Performance Security shall be valid until a date 28 days from the date of issue of the Certificate of Completion in the case of a Bank Guarantee, and until one year from the date of issue of the Completion Certificate in the case of a Performance Bond. |
| Dayworks | - If applicable, the Dayworks rates in the Contractor’s Tender shall be used only when the Project Manager has given written instructions in advance for additional work to be paid for in that way. - All work to be paid for as Dayworks shall be recorded by the Contractor on forms approved by the Project Manager. Each completed form shall be verified and signed by the Project Manager within two days of the work being done. - The Contractor shall be paid for Dayworks subject to obtaining signed Dayworks forms. |
| Cost of Repairs | - Loss or damage to the Works or Materials to be incorporated in the Works between the Start Date and the end of the Defects Correction periods shall be remedied by the Contractor at the Contractor’s cost if the loss or damage arises from the Contractor’s acts or omissions. |

E. Finishing the Contract

| Completion | - The Contractor shall request the Project Manager to issue a Certificate of Completion of the Works, and the Project Manager shall do so upon deciding that the whole of the Works is completed. |
| --- | --- |
| Taking Over | - The Employer shall take over the Site and the Works within seven days of the Project Manager’s issuing a certificate of Completion. |
| Final Account | - The Contractor shall supply the Project Manager with a detailed account of the total amount that the Contractor considers payable under the Contract before the end of the Defects Liability Period. The Project Manager shall issue a Defects Liability Certificate and certify any final payment that is due to the Contractor within 56 days of receiving the Contractor’s account if it is correct and complete. If it is not, the Project Manager shall issue within 56 days a schedule that states the scope of the corrections or additions that are necessary. If the Final Account is still unsatisfactory after it has been resubmitted, the Project Manager shall decide on the amount payable to the Contractor and issue a payment certificate. |
| Operating and Maintenance Manuals | - If “as built” Documentation and/or operating and maintenance manuals are required, the Contractor shall supply them by the dates stated in the PCC. - If the Contractor does not supply the “as built” Documentation and/or manuals by the dates stated in the PCC pursuant to GCC Sub-Clause 56.1, or they do not receive the Project Manager’s approval, the Project Manager shall withhold the amount stated in the PCC from payments due to the Contractor. |
| Termination | - The Employer or the Contractor may terminate the Contract if the other party causes a breach of the Contract. - Fundamental breaches of Contract shall include, but shall not be limited to, the following: - the Contractor stops work for 28 days when no stoppage of work is shown on the current Program/Works schedule and the stoppage has not been authorized by the Project Manager; - the Project Manager instructs the Contractor to delay the progress of the Works, and the instruction is not withdrawn within 28 days; - the Employer or the Contractor is made bankrupt or goes into liquidation other than for a reconstruction or amalgamation; - a payment certified by the Project Manager is not paid by the Employer to the Contractor within 84 days of the date of the Project Manager’s certificate; - the Project Manager gives Notice that failure to correct a particular Defect is a fundamental breach of Contract and the Contractor fails to correct it within a reasonable period of time determined by the Project Manager; - the Contractor does not maintain a Security, which is required; - the Contractor has delayed the completion of the Works by the number of days for which the maximum amount of liquidated damages can be paid, as defined in the PCC; - if the Contractor, in the judgment of the Employer, has engaged in Prohibited Practices, in competing for or in executing the Contract, then the Client may, after giving fourteen (14) days written notice to the Contractor, terminate the Contract and expel him from the Site. - When either party to the Contract gives notice of a breach of Contract to the Project Manager for a cause other than those listed under GCC Sub-Clause 55.2 above, the Project Manager shall decide whether the breach is fundamental or not. - Notwithstanding the above, the Employer may terminate the Contract for convenience. - If the Contract is terminated, the Contractor shall stop work immediately, make the Site safe and secure, and leave the Site as soon as reasonably possible. |
| Prohibited practices | 56.1 NEFCO requires that the Borrower (including the beneficiaries of NEFCO loans), as well as tenderers, suppliers, subsuppliers, contractors, subcontractors, concessionaires, consultants and subconsultants under NEFCO-financed contracts, observe the highest standard of ethics during the procurement and execution of such contracts. In pursuance of the NEFCO Policy on Anticorruption and Compliance (as defined in Clause 1.8 above), NEFCO: - (a) defines, for the purposes of this provision, the terms set forth below as follows: #### (i) “Abuse” means theft, misappropriation, waste or improper use of property or assets related to the Contract, either committed intentionally or through reckless disregard; #### (ii) “Coercion” means impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party for the purpose of improperly influencing the actions of a party; #### (iii) “Collusion” means an arrangement between two or more parties designed to achieve an improper purpose, including for the purpose of improperly influencing the actions of another party; #### (iv) “Corruption” means meaning the promise, offering, giving, receiving, or soliciting, directly or indirectly, anything of value or any undue advantage, or any act or omission that involves the abuse of authority or functions, for the purpose of influencing or causing to influence improperly the actions of another party, or for the purpose of obtaining an undue advantage for oneself or for another party; - “Fraud” means meaning any act or omission, including misrepresentation or concealing a material fact, that knowingly or recklessly misleads, or attempts to mislead, a party for the purpose of obtaining a financial or other benefit or undue advantage for oneself or for a third party, or to avoid an obligation; - “Obstruction” means #### (a) deliberately destroying, falsifying, altering or concealing evidence material to an investigation; #### (b) making false statements to investigators in order to materially impede an investigation; #### (c) failing to comply with requests to provide information, documents or records in connection with an investigation; #### (d) threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to a NEFCO investigation or from pursuing an investigation; or #### (e) materially impeding NEFCO’s contractual rights of audit or access to information; and - “Money Laundering” means #### (a) the conversion or transfer of property, knowing that such property is derived from criminal activity, to conceal and disguise the illicit origin of the property, or assisting any person who is involved in the commission of such activity to evade the legal consequences of this action; #### (b) the concealment or disguise of the true nature, source, location, disposition, movement, rights with respect to, or ownership of property, knowing such property is derived from criminal activity; #### (c) the acquisition, possession or use of property knowing, at the time of receipt, that such property was derived from criminal activity; or #### (d) participation or assistance in any of the activities above; and - (viii) “Financing of terrorism” means the provision or collection of funds, by any means, directly or indirectly, with the intention that they should be used or in the knowledge that they are to be used, in full or in part, in order to carry out terrorist activities (the "terrorist activities" shall have the same meaning as set out in Article 2 of the International Convention for the Suppression of the Financing of Terrorism). - (b) will cancel the portion of NEFCO financing allocated to a contract for Equipment or Related Works if it at any time determines that Prohibited Practices were engaged in by representatives of the Borrower or of a beneficiary of NEFCO financing during the procurement or the execution of that contract, without the Borrower having taken timely and appropriate action satisfactory to NEFCO to remedy the situation; - (c) may declare a firm/individual ineligible, either indefinitely or for a stated period of time, to be awarded a NEFCO-financed contract if it at any time determines that the firm/individual has engaged in Prohibited Practices in competing for, or in executing, a NEFCO-financed contract; and - (d) reserves the right, where a Borrower or a firm/individual has been found by a judicial process in any country or a finding by the enforcement (or similar) mechanism of another international organisation, including Mutual Enforcement Institutions, to have engaged in Prohibited Practices - (i) to cancel all or part of the NEFCO financing for such Borrower; and - (ii) to declare that such a firm/individual is ineligible, either indefinitely or for a stated period of time, to be awarded a NEFCO-financed contract. |
| Payment upon Termination | - If the Contract is terminated because of a fundamental breach of Contract by the Contractor, the Project Manager shall issue a certificate for the value of the work done and Materials ordered less advance payments received up to the date of the issue of the certificate and less the percentage to apply to the value of the work not completed, as specified in the PCC. Additional Liquidated Damages shall not apply. If the total amount due to the Employer exceeds any payment due to the Contractor, the difference shall be a debt payable to the Employer. - If the Contract is terminated for the Employer’s convenience or because of a fundamental breach of Contract by the Employer, the Project Manager shall issue a certificate for the value of the work done, Materials ordered, the reasonable cost of removal of Equipment, repatriation of the Contractor’s personnel employed solely on the Works, and the Contractor’s costs of protecting and securing the Works, and less advance payments received up to the date of the certificate. |
| Property | - All Materials on the Site, Plant, Equipment, Temporary Works, and Works shall be deemed to be the property of the Employer if the Contract is terminated because of the Contractor’s default. |
| Release from Performance | - If the Contract is frustrated by the outbreak of war or by any other event entirely outside the control of either the Employer or the Contractor, the Project Manager shall certify that the Contract has been frustrated. The Contractor shall make the Site safe and stop work as quickly as possible after receiving this certificate and shall be paid for all work carried out before receiving it and for any work carried out afterwards to which a commitment was made. |
| Suspension of NEFCO Loan | - In the event that NEFCO suspends the financing to the Employer, from which part of the payments to the Contractor are being made: - The Employer is obligated to notify the Contractor of such suspension within 7 days of having received the NEFCO’s suspension notice; - If the Contractor has not received sums due it within the 28 days for payment provided for in Sub-Clause 40.1, the Contractor may immediately issue a 14-day termination notice. |

| SectionVI. Particular Conditions of Contract |  |  |  |
| --- | --- | --- | --- |
| The following Particular Conditions of Contract shall supplement the GCC. Whenever there is a conflict, the PCC provisions shall prevail over. |  |  |  |
| A. General |  |  |
| GCC 1.1 (d) | The financing institution is: Nordic Environment Finance Corporation (NEFCO). |  |
| GCC 1.1 (r) | The Employer is: Ukraine executive body of Kyiv city council Kyiv city state administration municipal enterprise “Project implementation unit for the Kyiv public building energy efficiency project” Khmara Vyacheslav Valeriyovych - Director, Address: office № 305, 3A, B. Khmelnitskogo Street, Kyiv 01001 Phone: (044) 234-54-10 (27) Orlenko Serhii Volodymyrovych, Employer’s representative (on technical matters) adc@kyivesko.com.ua |  |
| GCC 1.1 (v) | The Intended Completion Date for the whole of the Works shall be [insert date]. |  |
| GCC 1.1 (y) | The Project Manager is Khmara Vyachesclav Valeriyovysch, Address: office № 303, 3A, B. Khmelnitskogo Street, Kyiv 01001 Phone: (044) 234-54-10 (27) Email: viacheslav.khmara@kyivesko.com.ua |  |
| GCC 1.1 (aa) | The Sites list is in accordance to Employer’s Requirements |  |
| GCC 1.1 (dd) | The Start Date shall be [insert date]. |  |
| GCC 1.1 (hh) | The Works consist of : Construction works on project «Capital repairs of individual heating substations and heating systems in public buildings of Kyiv» Lot 8.1 (11 Sites), as defined in Employer`s requirements and in Design documentation which is provided to Contractor |  |
| GCC 2.2 | Sectional Completions are: Not applied |  |
| GCC 2.3 | Documents that constitute the contract must be interpreted in following prioritized way: - Contract Agreement, - Letter of acceptance, - Letter of Tender, - Particular Conditions of Contract, - General Conditions of Contract, - Filled price schedule - Employer`s requirements - Works schedule - Contract price in form of local cost estimate - Design documentation |  |
| GCC 3.1 | The language of the contract is Ukrainian. The law that applies to the Contract is the law of Ukraine. |  |
| GCC 5.1 | The Project Manager may delegate any of his duties and responsibilities, particularly The Project Manager delegates his duties and responsibilities on Technical supervision to Technical supervision service (which is defined by Employer according to NEFCO`s procedures) according to current Ukrainian legislation |  |
| GCC 8.1 | Schedule of other contractors: Not applied |  |
| GCC 13.1 | The minimum insurance amounts and deductibles shall be: (a) for loss or damage to the Works and Materials, risks of fire, natural disasters, transport risks, illegal actions of third parties, water acts and from actions of third (construction works insurance): 100 (one hundred) % from Contract price b) For loss or damage to property (except the Works and Materials) in connection with Contract 50 (fifty) % from Contract price. |  |
| GCC 14.1 | Site Data are: list is specified in Employer`s requirements |  |
| GCC 18.2 | The Contractor shall provide the Employer with a written Health and Safety Policy and a project-specific Health and Safety Plan (the Plan) before the commencement of work. The Plan shall identify all risks specific and relevant to the project and shall provide information explaining how the identified risks will be managed by the Contractor. The Plan shall include details of the Contractor’s OHS management system, including the Contractor’s plans to manage and monitor the health and safety risks associated with all construction work under its control. The Plan shall be made available to NEFCO prior to the start of Construction Every Contractor shall plan, manage and monitor construction work carried out by him or under his control in a way which ensures that, so far as is reasonably practicable, it is carried out without risks to health and safety. In instances where the Contractor is a joint venture, consortium or a similar entity, the Contractor shall coordinate its planning, management and monitoring activities in a manner that will ensure that any overlap does not create any potential risks to third parties. All work related tasks shall be risk assessed before any work is undertaken. All significant hazards shall be identified and control measures introduced to reduce foreseeable risks of injury and ill health, so far is reasonable practicable. High regard shall be given in particular to assess and control the following specific activities and these shall be documented in the Health and Safety Plan; - Working at Heights; - Lifting Operations; - Movement of vehicles and mobile work equipment; - Ground disturbance and excavations; and, - Working with and around live electrical conductors. - Welding works The Contractor shall ensure that a safe and healthy working environment is provided, and that good international occupational health and safety practice is promoted. The Contractor shall take steps to prevent accidents, injury and disease arising in the course of work by identifying and controlling risks to workers, third parties and affected communities, so as far as is reasonably practicable. The Contractor shall ensure that all staff, labourers and persons entitled to be on site receive the necessary supervision, information, instruction and training to do their jobs in a manner that does not place themselves or third parties at risk. With regard to any unauthorised site visitors, the Contractor shall familiarise itself with, and comply with, any relevant provisions of the Applicable Law. Where appropriate, the Contractor shall provide equipment to minimise health and safety risks and enforce its use. The Contactor shall carry out a risk assessment to ensure the correct selection of equipment is made for every task. The work equipment shall be in good working condition, designed for the specific task and not improvised in any way. The Contractor shall put in place arrangements for emergency prevention, preparedness and response. |  |
| GCC 20.1 | The Sites access date is specified according to list in Employer’s requirements [insert date]. |  |
| GCC 23.1 | Any dispute arisen on Contract between Employer and Contractor should be settled according to judicial procedure in accordance with Ukrainian legislation. |  |
| GCC 23.2 | Not applied |  |
| GCC 24.3 | Hourly rate and types of reimbursable expenses to be paid to the Adjudicator: Not applied |  |
| B. Works execution Time Control |  |  |
| GCC 26.1 | The Contractor shall submit for approval a Program/Works schedule for the Works within 15 days from the date of the Letter of Acceptance. |  |
| GCC 26.3 | The period between Program/Works schedule updates is not applied. The amount to be withheld for late submission of an updated Program/Works schedule is not applied. |  |
| C. Quality Control |  |  |
| GCC 34.1 | The Defects Liability Period is: 24 months. |  |
| D. Cost Control |  |  |
| GCC 44.1 | The currency of the Employer’s country is: Hryvnia. |  |
| GCC 45.1 | The proportion of payments retained is: Not applied |  |
| GCC 46.1 | The liquidated damages for the whole of the Works are 0,5 % per week. The maximum amount of liquidated damages for the whole of the Works is 10% of the final Contract Price. |  |
| GCC 47.1 | The Advance Payments shall be: not more than 30 percent of the contract sum and shall be provided in two transactions. 1. First advance payment – not more than 15% of contract price shall be paid to Contractor not later than 30 calendar days after contract signing date on condition that Contract Performance Bank guarantee according to PCC (GCC 48.1) and insurance coverage according to PCC (GCC 13.1) are provided. 2. Second advance payment – not more than 15% of contract price shall be paid to Contractor not later than 10 calendar days after Employer receives documents confirming the use of the first advance payment (orders and payment documents for equipment and materialson this contract for sum not less than sum of the first advance payment) in the form acceptable for Employer (for example: duly certified contract copies, acceptance/delivery statements, original bank statements, invoices, etc.). |  |
| GCC 48.1 | The Performance Security amount is 5% from Contract price (a) Bank Guarantee: performance bond must be in form of unconditional bank Guarantee issued to Employer according to form and by bank acceptable by NEFCO. |  |
| E. Finishing the Contract |  |  |
| GCC 54.1 | The date by which operating and maintenance manuals are required is [insert date]. The date by which “as built” documentation are required is [insert date]. |  |
| GCC 54.2 | The amount to be withheld for failing to produce “as built” documentation and/or operating and maintenance manuals by the date required in GCC 54.1 is calculated in accordance with GCC 46.1. |  |
| GCC 55.2 (g) | The maximum number of days is: 45 days. |  |
| GCC 57.1 | The percentage to apply to the value of the work not completed, representing the Employer’s additional cost for completing the Works, is 20. |  |

Section VII. - Contract Forms

This Section contains forms which, once completed, will form part of the Contract. The forms for Performance Security and Advance Payment Security, when required, shall only be completed by the successful tenderer after contract award.

Letter of Acceptance

[ on letterhead paper of the Employer]

. . . . . . . [date]. . . . . . .

To:	. . . . . . . . . .  [name and address of the Contractor] . . . . . . . . . .

Subject:	. . . . . . . . . .   [Notification of Award Contract No].  . . . . . . . . . .

This is to notify you that your Tender dated . . . . [insert date] . . . .  for execution of the . . . . . . . . . .[insert name of the contract and identification number]. . . . . . . . . . for the Accepted Contract Amount of . . . . . . . . .[insert amount in numbers and words and name of currency], as corrected and modified in accordance with the Instructions to Tenderers is hereby accepted by us.

You are requested to furnish the Performance Security in the amount of [insert name of currency and amount (s) in figures and words] within 28 days in accordance with the Conditions of Contract, using for that purpose the Performance Security Form included in Section VII,PCC Supplement (Contract Forms).

In accordance with ITT 31.2 of the Tender Document you are requested to sign, date and return the Agreement within 28 days of receipt.

Signed by:

Name and Title of Authorised Signatory:

Name of Agency:

Attachment:  Contract Agreement

Contract Agreement

THIS AGREEMENT made the . . . . . .day of . . . . . . . . . . . . . . . . ., . . . . . . ., between . . . . . [name of the Employer]. . . . .. . . . . (hereinafter “the Employer”), of the one part, and . . . . . [name of the Contractor] . . . .(hereinafter “the Contractor”), of the other part:

WHEREAS the Employer desires that the Works known as . . . . . [name of the Contract]. . . . .should be executed by the Contractor, and has accepted a Tender by the Contractor for the execution and completion of these Works and the remedying of any defects therein, and the Employer agrees to pay the Contractor the Contract Price of [insert the accepted Contract Price in words and numbers]or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract

The Employer and the Contractor agree as follows:

1.	In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the Contract documents referred to.

2.	The following documents shall be deemed to form and be read and construed as part of this Agreement. This Agreement shall prevail over all other Contract documents, which shall apply in the following order.

- the Letter of Acceptance;

- the Letter of Tender ;

- the Amendments to Tender documents Nos _____[insert numbers of amendments if any];

- the Particular Conditions (PCC);

- the General Conditions of Contract (GCC);

- Filled in Price schedules;

- Employer’s requirements

- Works Schedules

- Contract price in form of local cost estimate

- Design documentation.

3.	In consideration of the payments to be made by the Employer to the Contractor as specified in this Agreement, the Contractor hereby covenants with the Employer to execute the Works and to remedy defects therein in conformity in all respects with the provisions of the Contract.

4.	The Employer hereby covenants to pay the Contractor in consideration of the execution and completion of the Works and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

IN WITNESS whereof the parties hereto have caused this Agreement to be executed in accordance with the laws of . . . . . [governing law in accordance with the PCC]. . . . .on the day, month and year specified above.

| Signed by: |  | Signed by: |  |
| --- | --- | --- | --- |
| for and on behalf of the Employer |  | for and on behalf the Contractor |  |

Performance Security (Bank Guarantee)

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	[insert name and Address of Employer]

Date:	_ [Insert date of issue]

PERFORMANCE GUARANTEE No.:	[Insert guarantee reference number]

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that [insert full name of Contractor] (hereinafter called "the Applicant") has entered into Contract No. [insert reference number of the contract] dated [insert date]with You for the execution of [insert name of contract and brief description of Works] (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, a Contract performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay You any sum or sums not exceeding in total an amount of [insert name of the currency and amount in figures],1 such sum being payable in the types and proportions of currencies in which the Contract Price is payable upon receipt by us of the Your complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying the demand, stating that the Applicant is in breach of its obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire, no later than the …. day of …… 2… 2, and any demand for payment under it must be received by us at this office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

_____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

one should note that according to the mentioned sub-clauses of the NEFCO’s Procurement Guidelines the company normally cannot be supplier of goods or works, if it had provided consultancy services to the Employer (e.g. development of design documentation) regarding the same goods and works

1	 The Guarantor shall insert an amount representing the percentage of the Accepted Contract Amount specified in the Letter of Acceptance, less provisional sums, if any, and denominated either in the currency(cies) of the Contract or a freely convertible currency acceptable to the Beneficiary.

2	Insert the date twenty-eight days after the expected completion date as described in GCC Clause 53.1. The Employer should note that in the event of an extension of this date for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph:  “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”